## Cover Page
P R O C U R E M E N T D O C U M E N T S
Volume
IV
:
BILL OF QUANTITIES
Procurement of
WATER AND SANITATION
DEVELOPMENT PROJECT
Construction Works for the Second
Baricho - Kakuyuni Water Supply
Project - Lot 1 (Second Baricho - Kakuyuni Pipeline)
ICB No: IDA - 6030 KE
Coast Water Works Development
Agency
KENYA

## PREAMBLE
PREAMBLE
1. These Bills of Quantities form part of the Contract Documents and are to be read in conjunction with the Conditions of Contract, Technical Specifications, and Drawings.
2. The quantities set forth in the Bills of Quantities represent the character of the work to be carried out with a reasonable factor of safety. There is no guarantee to the Contractor that he will be required to carry out the quantities of work indicated under any one particular item or group of items in the Bills of Quantities, though on the Contract as a whole the quantities are intended to represent the overall value of the work to be carried out.
3. The prices and rates inserted in the Bills of Quantities will be used for valuing the work executed and the Engineer will measure the whole of the works executed in accordance with the Contract.
4. The prices and rates inserted in the Bills of Quantities are to be the full inclusive costs of the works described under the items, complete in place and in accordance with the Specifications and Drawings, including setting out of the works, and including costs and expenses which may be required in, and for the construction of, the works described, together with any temporary works and installations which may be necessary and all general risks, liabilities and obligations set forth or implied in the Documents on which the Contract is based.
5. The brief descriptions in the items given in the Bills of Quantities are purely for the purpose of identification and in no way modify or supersede the detailed descriptions given in the Conditions of Contract, Specifications or Drawings. When pricing items, reference is to be made to the Conditions of Contract, Standard Specifications, Drawings and Special Specification for the full directions and description of work and materials.
6. A price or rate is to be inserted, in ink, against each item in the Bills of Quantities, whether quantities are stated or not, and if the Tenderer includes the cost of a particular item elsewhere in his rates or prices, he shall insert the word "nil" against both the rate and extension of that particular item. Should the Tenderer omit to price an item, then it will be assumed that he has included the cost of the item elsewhere in his rates or prices.
7. No alterations shall be made to the Bills of Quantities and no extra items shall be inserted. The Tenderer shall satisfy himself that the Contract Sum arrived at by pricing the quantities and items given is sufficient compensation for constructing and maintaining the whole of the works in accordance with the Contract Documents.
8. For the purpose of payment by Interim Certificate of "Lump Sum" or “sum” items the Engineer may assess the portion of the work completed on the "Lump Sum" or “sum” item and allow for payment of the portion the "Lump Sum" he deems fair and reasonable. The total of all portions allowed shall not exceed the "Lump Sum". All interim payments shall be subject to the retention stipulated in the Contract Documents.
9. During construction, the unit rate established for an item in one Bill of Quantities may be used as a basis for establishing a unit rate for similar work in another Bill of Quantities which contains no unit rate for the said item. No additional cost will be considered for such an eventuality.
10. The Contractor will be provided, by the Employer, with all that land occupied by the Permanent Works including the specified working width for pipe laying, treatment works and other permanent construction works. The costs of compensation and entry upon land (if any) for the specified working width will be paid by the Employer. All other costs for temporary access to the works or additional working space shall be paid by the Contractor.
11. It shall be the responsibility of the Contractor to arrange for the removal of, or alteration to, existing services where necessitated by the Works. Costs incurred will be borne by the Contractor.
12. Quantities for site clearance, stripping and spreading shall be based on the horizontal projection of the area cleared or stripped.
13. The rates for excavation items shall be deemed to include inter alia for setting aside spoil for reuse in the Works or disposing to approved tips, except where otherwise provided for in the Bills of Quantities.
14. Generally, excavation items are based on volumes for structures and on linear measurements for certain pipelines. The work may be covered by one or more items. The rates shall include as appropriate for:-
a) Breaking through surfaces, handling different classes of material separately; excavation beyond the net plan area of the foundations for working space and for battering or timbering etc.
b)Timbering
c)Dealing with water from any source whatsoever
d)Backfilling as specified
e)Disposal of surplus spoil
Measurement of volume of excavation for structures shall be calculated from the plan dimensions of the structure without allowance for working space.
The depth of excavation in pipe trenches will be measured from ground level to the invert of the pipes. Measurement for other excavations will be to the size which is required to accommodate the permanent works. A Tenderer shall accordingly allow in his prices for any amount of extra excavation, which may be necessary for working space to complete the work to the satisfaction of the Engineer.
Items are included for "Extra Over for Rock" on a volume basis. The rates shall include for breaking out and any other additional costs and the items shall apply to work encountered within measured excavation. Rock shall be measured as a volume calculated from the thickness encountered within the plan area of a mass excavation, within the plan dimensions of a structure, or within the nominal width of a trench. The decision of the Engineer on the classification of rock encountered in excavation shall be final and binding.
Timbering left in excavations shall only be measured for payment where it is specified or ordered by the Engineer.
15. When the site of any particular item of the Works has been sufficiently cleared of trees, undergrowth etc. and before any excavation or filling has been carried out, the Contractor shall carry out a survey under the supervision of the Engineer's Representative to take, record and agree upon an adequate number of original ground levels. The data so obtained shall be used as a basis for the computation of excavation and filling.
16. The volume of fill will be measured net to the finished levels as shown on the drawings or as amended by the Engineer.
17. The rates for concrete shall include for making and testing concrete cubes and forwarding the results to the Engineer. Testing is to be carried out by a Test Laboratory approved by the Engineer.
18. The rates for precast concrete paving shall include for all cutting, bedding, jointing and laying to falls.
19. The rates for precast concrete edging and kerbs shall include for formwork, concrete bed and backing, all cutting, bedding, jointing and laying to falls.
20. All formwork must be cleaned and oiled prior to use. All exposed concrete edges shall have a 20 mm chamfer unless otherwise directed. The formwork rates shall also be inclusive of all necessary box outs and cut outs for individual holes up to 1 square metre.
The rates for forming rebates in concrete walls etc. shall include for forming pockets for the fish tail fixing cleats where required.
Deductions from formwork quantities will be made for openings more than 1 square metre in area.
21. Formwork for upper surfaces inclined at 30 degrees or less to the horizontal is not measured and the cost of any such formwork used will be deemed to be included in the relevant concrete item rate.
22. Wrought formwork where specified will be measured to 150mm below final ground levels.
23. Items required for Structural Joints and Construction Joints shown on drawings shall be paid for as per the rates in the Bills of Quantities; the rate for providing and fixing PVC water bar being inclusive of all joints, overlaps, junctions, welding, formwork not shown on drawings shall be deemed to be included in the unit rates for concrete work.
24. All rates and sums in the Bills of Quantities shall be in Kenya Shillings and Cents.
25. A construction wayleave of up to 2 m for pipeline will generally be allowed.
Payment for site clearance is based upon this width except that the Engineer reserves the right to restrict this width due to the presence of obstructions, roads, houses and the like. Payment shall then be according to the actual area cleared. In case additional space is required this may be made available by the Contractor at his own cost.
No claim for additional space will be entertained by the Engineer. No claims for inconvenience and the like caused by obstruction will be entertained. The rates shall be deemed to include for reinstatement of fences, gates, etc.
26. All pipe diameters indicated in the Bills of Quantities and on Drawings are nominal for steel pipes and outside diameters for HDPE. Fittings dimensions to suit size/type of pipes supplied by the Tenderer and Tenderer’s rates are deemed to allow for this. No additional cost adjustment will be allowed.
27. Unless otherwise specified the method of measurement shall be in accordance with the Standard Method of Measurement of Civil Engineering Quantities (CESMM3) published by the Institution of Civil Engineers, London, Third Edition - 1991. In some cases variations to this method have been made to suit local practice. A Contractor shall be deemed to have priced the items accordingly and no claims relating to variation from the method of measurement stated in these documents shall be considered.
27.a Items for buildings, electrical and mechanical works are not described using CESMM3 for clarity purposes.
28. All quantities have been measured in Metric Units.
29. Explanation of abbreviations used in the Bills of Quantities is as follows:-
L.S-Lump Sum
PS- Provisional Sum
P.C.-Prime Cost
E.O.-Extra Over
Avg.-Average
Max.-Maximum
Min- Minimum
n.e.- Not Exceeding
nr- No.Number
mm- Millimetre
m-Linear Metre
m2 -Square Metre
m3- Cubic Metre
Ha.-Hectare
Drg.-Drawing
Kg.- Kilogramme
H.T.- High Tensile
M.S.-Mild Steel
B.L.- Bitumen Lined
Dia.-Diameter
E.C./EC- Epoxy Coated
E.L./EL- Epoxy Lined
S & S- Spigot & Socket
C.L.Cement-mortar Lined
C.I.-Cast Iron
D.I.-Ductile Iron
uPVC-Unplasticised Polyvinyl Chloride
HDPE-High Density Polyethylene
G.I.-Galvanised Iron
G.M.S.-Galvanised Mild Steel
P.E.H-.Palothene
PE-Polyethylene
Hr.-Hour
FE/-FeFerrous
OD-Outside Diameter
30. The rates for metalwork shall include for bolts, nuts, washers and ragbolts, fixing as specified or in accordance with the manufacturer's instructions and rectifying as specified any parts of the painted, coated or galvanised surface that may be damaged either before or after erection.
31. The rates for fixing penstocks and flap valves etc. shall include for bedding and grouting, testing for watertightness, greasing all working parts and leaving in good working order; where the item includes supply, the rates shall also include for supplying drawings for approval before manufacture is commenced.
32. Concrete Works
a) Item: Concrete |  | :
Unit: m3 of each class | :
Concrete shall be measured by the cubic metre of each class calculated from the dimensions given on the drawings or as instructed by the Engineer. No deduction shall be made in the measurement for:
i)bolt holes, pockets, box outs and cast-in components provided that the volume
of each is less than 0.15 cubic metres;
ii)Mortar beds, fillets, drip moulds, rebates, recesses, grooves, chamfers and thelike of 100mm total width of less;
like of 100mm total width of less;
iii)reinforcement.
The rates for concrete shall include for the cost of:
i)provision and transport of all materials including cement, aggregate water, etc
ii)admixtures and workability agents including submission of details unless specified
iii)batching, mixing, transporting, placing, compacting and curing;
iv)class UF1 finish;
v)laying to sloping surfaces not exceeding 15 degrees from the horizontal and laying to falls
vi)formwork to blinding concrete;
vii) placing and compacting against excavated surfaces where required including any additional concrete to fill overbreak or working space;
viii)complying with the requirements of Clauses 723, 401-415 inclusive and Clause 418 of the Specification
b) Item : Blinding Concrete
Unit : m3
Blinding concrete shall be measured by the cubic metre calculated as the product of the plan area of the foundation as shown on the drawings and the instructed thickness. No deduction shall be made for openings provided that the area of each is less than 0.5 square metres. Blinding concrete over hard material shall be measured as the volume used provided that the maximum thickness of 150mm allowed for overbreak is not exceeded.
The rate for blinding concrete shall include for all costs itemised in Note 32 a) of this Preamble.
c)Item : No Fines Concrete
Unit: m3 |  | :
No fines concrete shall be measured by the cubic metre calculated from the dimensions given on the drawings or as instructed by the Engineer.
The rate for no fines concrete shall include for all costs stated in Note 32 a) of this Preamble.
d)Item: Uniformed Surface Finish
Unit : m2 of each class of finish
Unformed surface finishes shall be measured by the square metre from the dimensions given on the drawings or as instructed by the Engineer.
The rate for concrete in Notes 32 a), b) and c) shall include for class UF1 finish.
The rate for unformed surface finishes shall include for the cost of complying with Clause 410 of the Specification.
e) Item : Formwork for Formed Surface Finishes
Unit: m2 of formwork for each class of finish for each range of inclinations
Except as stated below, formwork shall be measured by the square metre of formwork actually in contact with the finished face of the concrete. No deduction shall be made in the measurement for openings, pipes, ducts and the like, provided that the area of each is less than 0.50 square metres. Unless otherwise stated, if the volume or area of concrete has not been deducted when measuring the concrete in accordance with Notes 32 a), b) and c), formwork to form or box out the void shall not be measured.
Formwork less than 300mm high to edges of slabs shall be measured by the linear metre in accordance with Note 32 f) of this Preamble.
Inclined formwork shall be measured in accordance with the following classifications:
i) Horizontal: 85 to 90 degrees inclination from vertical
ii) Sloping: 10 to 85 degrees inclination from vertical
iii) Battered: 0 to 10 degrees inclination from vertical
iv) Vertical: 0 degrees
Sloping upper surfaces inclined at more than 15 degrees from the horizontal
Formwork required for blinding concrete, to form construction joints and shear keys for future concrete and other construction surfaces shall not be measured and the costs shall be included in the rates for other work.
Formwork to contraction and expansion joints shall be measured by the square metre on one face only. The rates shall include for the costs stated below and for forming recesses for sealant and channels for grout.
The rates for formwork shall include for the cost of submission of details, providing and transporting all materials for formwork and falsework, erection including provision of supports, fillets and chamfers 75mm and less in width, bolts, ties, fixings, cutting to waste, drilling or notching the formwork for reinforcement where required, working around pipes, ducts, conduits and waterstops, temporary openings, cleaning, dressing, stripping, filling bolt holes and any remedial work and for complying with Clauses 405, 407, 414, 415, 416, 418 and 501 t0 506 inclusive of the Specification.
f)Item :Formwork to Edges of Slabs |  | :
Unit: m of each class of finish |  | :
g)Item : Waterstops |  | :
Unit : m of each type |  | :
The rate for waterstops shall include for the provision, installation, jointing, any sealants required at the face of the concrete and for placing and compacting concrete around the waterstop.
h)Item: Mortar
Unit: m2
Mortar used for bedding base plates and the like shall be measured by square metre as the area of the base plate at the specified nominal thickness of bedding.
Mortar used in filling bolts pockets and the like shall not be measured separately and the costs shall be included in the rates for the bolts.
The rates for mortar shall include for the cost of providing and placing the mortar and of complying with the requirements of Clauses 411 and 417 of the Specification.
i)Item: Admixture Workability and Hardening Agents
Unit: As specified in the Special Specification
Where required by the Special Specification admixtures, workability and hardening agents shall be measured and paid for in accordance with the Special Specification.
j)Item: Reinforcement
Unit: Tonne of each type for each range of diameters
Reinforcement shall be measured separately for each of the following ranges:
i)of diameter equal to or less than 16mm
ii)of diameter greater than 16mm
Steel fabric reinforcement shall be measured in accordance with Note 32 k) of this Preamble.
Steel (plain and deformed bars) reinforcement shall be measured by the tonne and shall be the calculated weight of the steel required including splice lengths shown on the drawings. No allowance shall be made in the measurement for rolling margins or cutting waste. The density of steel shall be taken as 7850 kilogrammes per cubic metre.
The rates for reinforcement shall include for cost of providing, cutting to length, splice lengths additional to those shown on the drawings, laps, bending, hooking, waste incurred by cutting, cleaning, spacer blocks, provision and fixing of chairs or other types of supports, welding, fixing the reinforcement in position including the provision of wire or other material for supporting and tying the reinforcement in place, being reinforcement aside temporarily and straightening, placing and compacting concrete around reinforcement and for complying with the requirements of Clauses 419 to 420 inclusive of the Specification
k)Item: Fabric Reinforcement
Unit: m2 of each type
Steel fabric reinforcement shall be measured by the square metre and shall be the calculated area excluding any allowance for laps.
The rate for steel fabric reinforcement shall include for the costs stated in Note 32 j) of this Preamble.
Sewers, Drains and Pipelines
33. The rates for pipes, pipework and specials shall include for supply of all materials, excavating, laying jointing and backfilling pipes in ordinary soil material. The rates shall also include for all cutting of pipes consequent upon structures, specials and fittings being constructed in the designated positions.
34. The rates for concrete surround, bed and haunching to pipes, concrete in anchor blocks to pipes, and to gully pots shall include for all formwork required and for any additional concrete the Contractor may place for his own convenience or by reason of the method of carrying out the work.
35. Pipes, Fittings and Valves
a) uPVC pipes and fittings to SRN 300 Class ‘D’ (12 bar), or as specified
HDPE pipes and fittings to BS 6572 Standards Class ‘E’ (16 bar), or as specified
b)Steel pipes and fittings to SRN 210, SRN 212 and SRN 216
c)Ductile Iron (DI) pipes and fittings to SRN 202
d)Galvanised Iron (GI) pipes and fittings to SRN 203
e)Flexible joint spigot and socket precast concrete (PVC) pipes to SRN 409
Rigid joint spigot and socket pcc pipes to SRN 409
Ogee joint pcc pipes to SRN 407
f)All flanges to SRN 207, NP 16 or as specified
g)Gate valves to SRN 501, NP 16 or as specified
h)Double orifice air valves as specified
Single large orifice air valves as specified
Single small orifice air valves as specified
i)Fire hydrants to SRN 509
j)Butterfly valves to SRN 506, NP 16 as specified
k)Ball float valves as specified
l)All pipe, fittings and valve diameters indicated are nominal diameters. For relevant outside diameters see following pages
m)Supply of pipes and fittings to include for cost of supply of all jointing materials like bolts, nuts, washers, gaskets, packings, jointing glue, etc.
n)uPVC pipes to be supplied complete with compression joints
o)Supply of C/L steel pipes to be with flange or push-in joints. If plain ended pipes are offered, one number coupling per length is to be included. Coupling is subject to approval by the Engineer
p)Ductile Iron pipes to be supplied with push-in type joints
q)Galvanised Iron pipes to be with threaded coupling joints, or as specified
r)Precast concrete ogee pipes to be supplied complete with all jointing materials
uPVC PIPES TO SRN 300
OUTSIDE PIPE DIAMETER NOMINAL INTERNAL
AS PER SRN 300 (mm) DIAMETER (mm)
P 63 50
P 75 65
P 90 80
P 110 100
140 125
P 160 150
P 225 200
P 280 250
P 315 300
355 350
P = Preferred sizes as per MWI Water Design Manual
CEMENT-MORTAR LINED STEEL PIPES TO SRN 212
OUTSIDE PIPE DIAMETER NOMINAL INTERNAL
AS PER SRN 300 (mm) DIAMETER (mm)
60.3 50
76.1 65
88.9 80
114.3 100
139.7 125
168.3 150
193.7 175
219.1 200
244.5 225
273 250
323.9 300
355.6 350
406.4 400
457 450
508 500
559 550
610 600
DUCTILE IRON PIPES TO SRN 202
OUTSIDE PIPE DIAMETER NOMINAL INTERNAL
AS PER SRN 300 (mm) DIAMETER (mm)
66 50
82 65
98 80
118 100
144 125
170 150
222 200
274 250
326 300
378 350
429 400
480 450
532 500
635 600
Shop Drawings
36. Detailed shop drawings, in triplicate, to be provided for all items where ferrous pipework, fittings and any metalwork i.e. penstocks, ladders etc., are indicated to be installed as outlined in the bills of quantities and drawings. These drawings to be submitted well in advance of ordering the above materials and the billed rates are deemed to include for provision of these drawings, samples where requested, and inspection where fabricated by the Engineer or his Representative.
Prime Cost Items
37. Attendance on nominated Sub-Contractors shall include for all or any of the following as appropriate - labour, materials and plant required for taking delivery, carting, storing, hoisting and builder's work entailed in fixing, erecting and installing as specified or in accordance with the manufacturer's instructions and all overheads and profits.
38. When, in the opinion of the Engineer, it is reasonable to expect the Contractor to price the attendance item it will be so included in the Bills of Quantities. In all other cases it will form the subject of a Provisional Sum to be expended on a Dayworks basis.
39. Profit shall include for establishment charges, profit and any other costs not included in the attendance item.
40. The rates for the supply of any mechanical and electrical equipment shall include for the submission of factory test results.
41. Definitions of Terms used in Bill of Quantities
a)‘Provide’ - shall mean all costs to cover purchase of materials in good condition, services for transaction with the supplier, supervision, transport to site of works all charges for rental, consumptions, overheads and profits throughout the Contract. It shall also include for all maintenance, insurance and handling and storage whenever applicable.
b)‘Excavate for’ - shall mean handling of any material from its incumbent position intended for specified work shown in the drawings or directed by the Engineer and backfilling and compacting part of material after laying of pipes or erection of structures, and cart away remaining to tips to be provided by the Contractor. The cost for this work shall include all survey, supervision, labour, tools, machinery, protection of work, pumping, insurances and overheads and profits.
c)‘Laying’ - shall cover all work necessary for placing an object or material to true line and level specified in a drawing or as directed by the Engineer.
d)‘Jointing’ - shall mean process of fixing specified material, pipes, fittings and specials together using appropriate tools, material, labour and machinery. It should cover for all work necessary to provide matching of opposite parts in size, shape and position indicated and clamps, seatings and holders to hold firmly.
e) ‘Testing’ - shall mean provision of all materials, apparatus, labour, machinery, charges for the media or chemical to be used and their transport, repair of object to be tested if required, re-testing, excavation of any part for visual inspection, erection of any type all until the object has been certified as having passed the required test satisfactorily.
f) ‘Install’ - shall include for all work requirements stipulated for "laying" and "jointing". It will cover all expenses for the provision of labour, materials, removal from stores, complete erection, installation, supervision, site testing and commissioning as per the Specifications.

## Summary
SECOND BARICHO KAKUYUNI WATER SUPPLY PROJECT
GRAND SUMMARY
BILL No. | DESCRIPTION | AMOUNT (KShs)
1 | Preliminary and General Items (P&G)
2 | Rising Main | 0
3 | 5,000 m3 Kakuyuni Reservoir | 0
4 | Pump Station | 0
5 | Day Works | 0
| 10% CONTIGENCIES | 0
| Sub Total 2 | 0
| 16% VAT | 0
| GRAND TOTAL | 0

## Bill No. 1 - P & G
BILL No. 1 - PRELIMINARIES AND GENERAL ITEMS
ITEM | DESCRIPTION | UNIT | QTY | RATE (KShs) | AMOUNT (KShs)
CLASS A - GENERAL ITEMS
1A1 | Contractual Requirements
Allow for Provision of:
1A110 | Perfomance Security | Item | L.S | - | -
1A120.1 | Insurance of Works and Contractor's Equipment as per Clause 18.2 of Conditions of Contract. | Item | L.S |  | 0
1A120.2 | Insurance against Injuty to Third Party Persons and Damage to Property as per Clause 18.3 of Conditions of Contract. | Item | L.S |  | 0
1A120.3 | Insurance for Contractor's Personnel as per Clause 18.4 of Conditions of Contract | Item | L.S |  | 0
1A2 | Specified Requirements
1A21 | Offices and Accomodation for the Engineer's Staff
1A211 | Provide all materials and construct offices for the Resident Engineer at a site provided by the Employer and as detailed in the Book of Drawings and according to the specifications, total floor area of 250 m2. The office shall revert to the Employer at the end of the Contract. | Item | L.S
1A212 | Provide Furniture and equipment for the Engineer's office as detailed in the specification. Furniture and equipment to revert to the Employer at the end of the Contract. | Item | PS | 2000000 | 2000000
1A213 | Provide or Rent and maintain fully furnished and functional 4No. Residential House for Resident Engineer's Team to the approval of the Engineer. | month | 12 | 350000 | 4200000
1A214 | Allow for Contractor's overhead and profit for item 1A212 - 1A213 | % | 6200000 |  | 0
1A22 | Services for Engineer's Staff
1A221 | Provisional sum for purchase and Supply 4 No. new 4WD Project Vehicles: 3 No. double Cabin vehicles and 1 No. Station Wagon (utility) vehicle; all diesel engines and capacity 2500cc - 2800cc vehicles, all for the exclusive use by the Engineer. The vehicles are to revert to the Empoyer at the end of the project. The vehicles are subject to approval by the engineer. | P-Sum | 1 | 35000000 | 35000000
0
1A222 | Allow for Contractor's overheads and profit for item 1A221 | % | 35000000 |  | 0
1A223 | Hire or provide vehicles for period not exceeding 3 months before procuring vehicles for Engineer. The vehicles are subject to approval by the Engineer | Month | 3 |  | 0
PAGE TOTAL TAKEN TO P&G COLLECTION PAGE
BILL No. 1 - PRELIMINARIES AND GENERAL ITEMS
ITEM | DESCRIPTION | UNIT | QTY | RATE (KShs) | AMOUNT (KShs)
1A224 | Maintain, insure, fuel, lubricate and servicing of the transport vehicles as per item 1A221 for the Contract Period - Allow approximately 7,500 km per vehicle month | Vehicle month | 12 |  | 0
0
1A225 | Extra over for mileage over 7,500km per vehicle per month | km | 15000 |  | 0
1A226 | Allow a provisional sum of KES 1,000,000 Engineer's Representative office communication, internet, telephone, airtime charges for duration of the assignment. | P-sum | 1 | 1000000 | 1000000
1A221.5 | Allow for Contractor's overhead and profit for item 1A226 | % | 1000000 |  | 0
1A227 | Provision of Engineer's Representative's office consumables: tea, drinking water, toiletry etc during the Contract Period | Month | 12
1A228 | Provision for payment of services (Water, Security and Electricity) to the Resident Engineer's Office during the Contract Period | Month | 12
Equipment for Engineer's Staff
1A231.1 | Allow for monthly maintenance of office equipment (stationery, printers, cameras etc) for use by the Engineer's Staff | month | 12 | 60000 | 720000
1A231.2 | Allow for Contractor's overhead and profit for item 1A231.1 | % | 720000 |  | 0
1A233 | Provide and maintain of surveying instruments (RTK type, to be specified by the Engineer) for the use of the Engineer's staff (Provisional). Ownership to revert to the Employer. | Item | 1 |  | 0
1A24 | Attendance Upon Engineer's Staff
Provide the following Staff for the Resident Engineer's Office. (Note: The Staff to be employed by the Contractor but to be under the exclusive day to day instruction of the Resident Engineer).
1A240 | 1No. Office Secretary. | Month | 12
1A240.1 | 1No. Office Assistant. | Month | 12
1A241 | 4No. Drivers - (4Nr x 12 months each). | Month | 48
1A242 | 3No. Three Chainmen - (3Nr x 12 months each). | Month | 36
1A24.1 | Allow for Contractor's overhead and profit for item 1A240 - 1A242 | % | 0
PAGE TOTAL TAKEN TO P&G COLLECTION PAGE
BILL No. 1 - PRELIMINARIES AND GENERAL ITEMS
ITEM | DESCRIPTION | UNIT | QTY | RATE (KShs) | AMOUNT (KShs)
Testing of Materials and Works
1A250.1 | Provisional sum of KES 500,000 for testing of materials as specified or directed by the Engineer | sum | 1 | 500000 | 500000
1A250.2 | Allow for Contractor's overhead and profit for item 1A250.1 | % | 500000 |  | 0
1A27 | Temporary Works
1A270 | Provision, fixing, maintaining and removal of Project Publicity signboards and plaque | nr | 5 |  | 0
1A271 | Provisional Sum for Traffic Diversions,Traffic regulation; establishment, operation and removal as directed by the Engineer | Item | LS
Other Provisional sums
1A279.1 | Provisional Sum of KES 5,000,000 for fees requested by various authorities and agencies | sum | 1 | 5000000 | 5000000
1A279.2 | Allow a provisional sum of Kshs. 5,000,000 for Inspection and Witness Testing of Pipes, Fittings,Pumps and Equipment at manufacturer's premises by the Employer, Engineer and their representatives. | PC | 1 | 5000000 | 5000000
1A279.3 | Allow for Contractor's overhead and profit for item 1A279.1 - 1A279.2 | % | 10000000 |  | 0
1A279.4 | Allow a provision for the Preparation of the As-Built Drawings by the time of commissioning of the Works in accordance with Clause 58.1 of GCC | LS
Method Related Charges
In addition to the items listed hereunder, a tenderer is to insert such items as he may decide to cover, items of work relating to his intended method of executing the works, costs of which are not to be considered as allowed in the rates and prices for the other items.
Accomodation, Buildings and Services
1A310 | Establish, maintain and remove Contractor's camp including offices, stores, laboratories, cabins, canteens etc and services including electricity, water, security, transport, staff welfare etc | Item | LS
PAGE TOTAL TAKEN TO P&G COLLECTION PAGE
BILL No. 1 - PRELIMINARIES AND GENERAL ITEMS
ITEM | DESCRIPTION | UNIT | QTY | RATE (KShs) | AMOUNT (KShs)
1A41.3 | Allow a provisional sum of Kshs. 1,500,000 to cover facilitation for the Project Management by the Employer's team as directed by the Project Manager. | PS | 1 | 1500000 | 1500000
1A41.4 | Allow a Provisional sum of Kshs. 2,500,000 to cater for (monthly site meetings, site visits by government officials, project ground breaking/commission etc as directed by the project manager | PS | 1 | 2500000 | 2500000
1A 420.1 | PC Sum of Kshs. 1,000,000 for provision of communication facilities for the Project Supervision staff/Employers staff as directed by the project manager | PC | 1 | 1000000 | 1000000
1A42.2 | Allow a Provisional Sum of Kshs. 2,000,000 for Implementation of EHS and C-ESMP while undertaking the works including facilitation for stakeholders liaison, community consultation and any other related mobilization for smooth execution of the works. | PS | 1 | 2000000 | 2000000
1A42.5 | Allow a Provisional sum of Kshs. 1,500,000/- , to be spent in whole or part, for confirmatory geotechnical investigations to be undertaken as directed by the Engineer. | PS | 1 | 1500000 | 1500000
1A42.6 | Allow provisional sum of kshs. 10,000,000 to be spent in whole or part, for Project's Corporate Social Responsibility to the Kakuyuni High School in Constructing a 96 capacity dormitory with beds. This expense will be expended as directed by the Project Manager | PS | 1 | 10000000 | 10000000
1A42.7 | Allow provisional sum of kshs. 15,000,000 to be spent in construction of staff Houses Grade 9(Type D houses each) 2Nr Unit (with 2 Houses each.) Include for Building and Provision of plumbing works,inspection chambers,sewer pipes,water supply and electrical installation,furniture and other facilities all to the approval of Engineer. | PS | 1 | 15000000 | 15000000
1A42.8 | Allow for Contractor's overhead and profit for item 1A41.3-1A42.7 | % | 33500000 |  | 0
PAGE TOTAL TAKEN TO P&G COLLECTION PAGE
BILL NO. 1 - PRELIMINARIES AND GENERAL ITEMS
ITEM | DESCRIPTION | UNIT | QTY | RATE (KShs) | AMOUNT (KShs)
BILL 1 SECTION COLLECTION PAGE
1 | BROUGHT FORWARD FROM PAGE 1 |  |  |  | 0
2 | BROUGHT FORWARD FROM PAGE 2 |  |  |  | 0
3 | BROUGHT FORWARD FROM PAGE 3 |  |  |  | 0
4 | BROUGHT FORWARD FROM PAGE 4 |  |  |  | 0
| PAGE TOTAL TAKEN TO GRAND SUMMARY PAGE |  |  |  | 0

## BILL NO. 5 RISING MAIN (hidden)
BILL 5 - RISING MAIN
ITEM | DESCRIPTION | UNIT | QTY | RATE (KShs) | AMOUNT (KShs)
CLASS A: GENERAL ITEMS
Specified Requirements
Testing of works
Carry out pressure testing, cleansing and sterilising of the pipeline in accordance with clauses 440 and 441 of the specification.
3A260.1 | DN500 steel pipes to 200m maximum test pressure | m | 5020 | 600 | 3012000
CLASS D:DEMOLITION AND SITE CLEARANCE
30120
3D100 | General clearance for pipeline for full width of easement including grubbing out all shrubs etc and removal of all trees of girth < 0.5m | ha | 4 | 200000 | 800000
3D210 | Tree girth 0.5 - 1.0m | nr | 20 | 4000 | 80000
3D220 | Tree girth 1.0 - 2.0m | nr | 15 | 8000 | 120000
3D310 | Tree girth 2.0 - 3.0m | nr | 10 | 12000 | 120000
CLASS I: PIPEWORK - PIPES
PN20 Pipes, cement mortar lined and epoxy coated socket to spigot with rubber ring jointed to Clause 408: Supply and transport pipes, break out surface, excavate trench, cut and lay pipes, backfill with selected material from the trench excavations and compact, disposal of surplus all as specified, shoring Sides of Excavation trenches, Backfilling and final Reinstatement.
2I441.1 | Nominal bore 500mm not in trenches | m | 20 | 20465 | 409300 | 3000 | [12 empty] | 0 |  |  |  | 0 |  |  | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0
[19 empty] | 0 |  |  |  | 0 |  |  | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0
2I442.1 | Nominal bore 500mm in trenches, depth not exceeding 1.5m | m | 820 | 21100 | 17302000 | [13 empty] | 0 |  |  |  | 0 |  |  | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0
[19 empty] | 0 |  |  |  | 0 |  |  | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0
2I443.1 | -Ditto- but depth 1.5m - 2m | m | 950 | 21405 | 20334750 | [6 empty] | 570 | 12200850 | 570 | 12200850 |  | 0 | 570 | 12200850 |  | 0 | 570 | 12200850 |  | 0 | 570 | 12200850 | 500 | 10702500 | 1070 | 22903350 | 970 | 20762850 | 2040 | 43666200 |  | 0 | 2040 | 43666200 |  | 0
[13 empty] | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0
2I444.1 | -Ditto- but depth 2.0m - 2.5m | m | 1110 | 22100 | 24531000 | [6 empty] | 1220 | 26962000 | 1220 | 26962000 | 500 | 11050000 | 1720 | 38012000 |  | 0 | 1720 | 38012000 | 1000 | 22100000 | 2720 | 60112000 | 1000 | 22100000 | 3720 | 82212000 |  | 0 | 3720 | 82212000 |  | 0 | 3720 | 82212000 | 95 | 2099500
[13 empty] | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0
2I445.1 | -Ditto- but depth 2.5m - 3.0m | m | 1210 | 22850 | 27648500 | [6 empty] | 440 | 10054000 | 440 | 10054000 | 934 | 21341900 | 1374 | 31395900 |  | 0 | 1374 | 31395900 |  | 0 | 1374 | 31395900 |  | 0 | 1374 | 31395900 | 585 | 13367250 | 1959 | 44763150 |  | 0 | 1959 | 44763150 | 85 | 1942250
[13 empty] | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0
2I446.1 | -Ditto- but depth 3.0m - 3.5m | m | 760 | 24200 | 18392000 | [6 empty] | 160 | 3872000 | 160 | 3872000 |  | 0 | 160 | 3872000 |  | 0 | 160 | 3872000 |  | 0 | 160 | 3872000 |  | 0 | 160 | 3872000 | 385 | 9317000 | 545 | 13189000 |  | 0 | 545 | 13189000 |  | 0
[14 empty] | 0 |  |  |  | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 |  | 0 |  | 0
2I447.1 | -Ditto- but depth 3.5m - 4.0m | m | 200 | 25585 | 5117000 | [11 empty] | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0
[19 empty] | 0 |  |  |  | 0 |  |  | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0
2I448.1 | -Ditto- but depth exceeding 4m | m | 50 | 27150 | 1357500 | [13 empty] | 0 |  |  |  | 0 |  |  | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0
3I011 | DN 80 in trenches depth n.e 1.5m. | m |  | 600 | 0
3I031 | DN 400 in trenches depth n.e 1.5m. | m |  | 840 | 0
3I032 | Ditto but depth 1.5 - 2m | m |  | 1050 | 0
3I033 | Ditto but depth 2.0 - 2.5m | m |  | 1500 | 0
3I033 | Ditto but depth 2.5 - 3.0 m | m |  | 1800 | 0
| PAGE TOTAL CARRIED TO COLECTION PAGE |  |  |  | 119224050
BILL 5 - RISING MAIN
ITEM | DESCRIPTION | UNIT | QTY | RATE (KShs) | AMOUNT (KShs)
3I033 | Ditto but depth 3.0 - 3.5m | m |  | 2100 | 0
CLASS J: PIPEWORK - FITTINGS AND VALVES
All steel fittings to be Epoxy Coated and Lined. Flanges to NP20 for all fittings and valves
Rates to include for provision and fixing. Flanges to PN 10 steel unless otherwise stated
Bends - Short Radius
Single flanged
3J311 | DN 80 GS, 90o | nr |  | 6000 | 0
| Pipeline Horizontal and Vertical Bends | [17 empty] | 0 |  |  |  | 0 |  |  | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0
[19 empty] | 0 |  |  |  | 0 |  |  | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0
2J313.1 | Nominal bore 500mm double socketted 11¼o bend | nr | 7 | 54845 | 383915 |  |  | 34 | 1864730 | 34 | 1864730 | 70 | 2380 | 104 | 1867110 | 22 | 1206590 | 126 | 3073700 |  | 0 | 126 | 3073700 |  | 0 | 126 | 3073700 |  | 0 | 126 | 3073700 |  | 0 | 126 | 3073700 |  | 0 | 126 | 3073700 |  | 0
|  |  | 0 | [15 empty] | 0 |  |  |  | 0 |  |  | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0
2J313.2 | Nominal bore 500mm double socketted 22½o bend | nr | 10 | 57585 | 575850 |  |  | 6 | 345510 | 6 | 345510 | 14 | 84 | 20 | 345594 | 14 | 806190 | 34 | 1151784 |  | 0 | 34 | 1151784 |  | 0 | 34 | 1151784 |  | 0 | 34 | 1151784 |  | 0 | 34 | 1151784 |  | 0 | 34 | 1151784 |  | 0
|  |  | 0 | [15 empty] | 0 |  |  |  | 0 |  |  | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0
2J313.3 | Nominal bore 500mm double socketted 30o bend | nr | 7 | 60500 | 423500 | [13 empty] | 0 |  |  |  | 0 |  |  | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0
|  |  | 0 | [15 empty] | 0 |  |  |  | 0 |  |  | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0
2J313.4 | Nominal bore 500mm double socketted 45o bend | nr | 12 | 66500 | 798000 | [13 empty] | 0 |  |  |  | 0 | 25 | 1662500 | 25 | 1662500 | 35 | 2327500 | 60 | 3990000 | 18 | 1197000 | 78 | 5187000 | 5 | 332500 | 83 | 5519500 | 4 | 266000
|  |  | 0 | [15 empty] | 0 |  |  |  | 0 |  |  | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0
2J313.5 | Nominal bore 500mm double socketted 90o bend | nr | 16 | 73165 | 1170640 | [10 empty] | 3 | 219495 | 3 | 219495 | 14 | 1024310 | 17 | 1243805 | 8 | 585320 | 25 | 1829125 | 5 | 365825 | 30 | 2194950 |  | 0 | 30 | 2194950 |  | 0 | 30 | 2194950 | 2 | 146330
Plain ended
3J313.1 | DN 400, 45o | nr |  | 30000 | 0
3J313.2 | DN 400, 30o | nr |  | 21000 | 0
3J313.2 | DN 400, 22.5o | nr |  | 21000 | 0
3J313.3 | DN 400, 11.25o | nr |  | 21000 | 0
| Air Valves and Washouts Fittings | [17 empty] | 0 |  |  |  | 0 |  |  | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0
[19 empty] | 0 |  |  |  | 0 |  |  | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0
| Bends (NP20) | [17 empty] | 0 |  |  |  | 0 |  |  | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0
[19 empty] | 0 |  |  |  | 0 |  |  | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0
2J311.1 | Nominal bore 100mm, flanged plain ended 90o bend (for Type 1 Washouts) | nr | 3 | 11565 | 34695 | [13 empty] | 0 |  |  |  | 0 |  |  | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0
|  |  | 0 | [15 empty] | 0 |  |  |  | 0 |  |  | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0
2J311.2 | Nominal bore 100mm, double flanged long radius 90o bend (for air valves vents) | nr | 3 | 13875 | 41625 | [13 empty] | 0 |  |  |  | 0 |  |  | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0
|  |  | 0 | [15 empty] | 0 |  |  |  | 0 |  |  | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0
| Junctions and Branches (NP20) |  | 0 | [15 empty] | 0 |  |  |  | 0 |  |  | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0
|  |  | 0 | [15 empty] | 0 |  |  |  | 0 |  |  | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0
2J323.1 | Nominal bore 500mm x 100mm double socket tee with flanged branch tee (for Air Valves) | nr | 3 | 67400 | 202200 |  |  | 8 | 539200 | 8 | 539200 | 15 | 1011000 | 23 | 1550200 | 12 | 808800 | 35 | 2359000 |  | 0 | 35 | 2359000 |  | 0 | 35 | 2359000 |  | 0 | 35 | 2359000 |  | 0 | 35 | 2359000 |  | 0 | 35 | 2359000 |  | 0
|  |  | 0 | [15 empty] | 0 |  |  |  | 0 |  |  | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0
2J323.2 | Nominal bore 500mm x 100mm double socket with flanged branch level invert tee (for Washouts) | nr | 3 | 67400 | 202200 |  |  | 6 | 404400 | 6 | 404400 | 12 | 808800 | 18 | 1213200 | 8 | 539200 | 26 | 1752400 |  | 0 | 26 | 1752400 |  | 0 | 26 | 1752400 |  | 0 | 26 | 1752400 |  | 0 | 26 | 1752400 |  | 0 | 26 | 1752400 |  | 0
0
| Double Collars to PN20 as specified |  | 0 | [15 empty] | 0 |  |  |  | 0 |  |  | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0
|  |  | 0 | [15 empty] | 0 |  |  |  | 0 |  |  | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0
2J341.1 | Nominal bore 100mm flexible coupling | nr | 3 | 5385 | 16155 | [13 empty] | 0 |  |  |  | 0 |  |  | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0
|  |  | 0 | [15 empty] | 0 |  |  |  | 0 |  |  | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0
2J344.1 | Nominal bore 600mm flexible coupling | nr | 12 | 31765 | 381180 | [13 empty] | 0 |  |  |  | 0 |  |  | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0
|  |  | 0 | [15 empty] | 0 |  |  |  | 0 |  |  | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0
| Adaptors (NP20) |  | 0 | [15 empty] | 0 |  |  |  | 0 |  |  | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0
|  |  | 0 | [15 empty] | 0 |  |  |  | 0 |  |  | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0
2J351.1 | Nominal bore 100mm flange adaptor | nr | 3 | 4250 | 12750 | [13 empty] | 0 |  |  |  | 0 |  |  | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0
|  |  | 0 | [15 empty] | 0 |  |  |  | 0 |  |  | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0
| Straight Specials to PN20 Pressure as specified |  | 0 | [15 empty] | 0 |  |  |  | 0 |  |  | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0
|  |  | 0 | [15 empty] | 0 |  |  |  | 0 |  |  | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0
2J381.1 | Nominal bore 100mm diameter socket to spigot piece with thrust flange, 900mm long-WO | nr | 3 | 5085 | 15255 | [13 empty] | 0 |  |  |  | 0 |  |  | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0
|  |  | 0 | [15 empty] | 0 |  |  |  | 0 |  |  | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0
2J381.2 | Nominal bore 100mm diameter double spigot piece, 15000mm long-WO | nr | 3 | 30520 | 91560 | [13 empty] | 0 |  |  |  | 0 |  |  | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0
0
2J383.1 | Nominal bore 100mm diameter double flanged riser piece, 2000mm long- Cut to suit-AV | nr | 3 | 16250 | 48750 | [13 empty] | 0 |  |  |  | 0 |  |  | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0
|  |  | 0 | [15 empty] | 0 |  |  |  | 0 |  |  | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0
2J481.1 | Nominal bore 150mm uPVC pipe sleeve over washout valves, 3m long | nr | 3 | 3450 | 10350 | [13 empty] | 0 |  |  |  | 0 |  |  | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0
|  |  | 0 | [15 empty] | 0 |  |  |  | 0 |  |  | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0
| Valves to PN 20 Pressure as specified |  | 0 | [15 empty] | 0 |  |  |  | 0 |  |  | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0
|  |  | 0 | [15 empty] | 0 |  |  |  | 0 |  |  | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0
2J811.1 | Nominal bore 100mm double flanged isolating Valve (for air valves) | nr | 3 | 42000 | 126000 | [13 empty] | 0 |  |  |  | 0 |  |  | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0
|  |  | 0 | [15 empty] | 0 |  |  |  | 0 |  |  | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0
2J811.2 | Nominal bore 100mm double flanged Gate Valve (for washouts) | nr | 3 | 45000 | 135000 | [13 empty] | 0 |  |  |  | 0 |  |  | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0
|  |  | 0 | [15 empty] | 0 |  |  |  | 0 |  |  | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0
| Air Valves to PN 20 Pressure as specified |  | 0 | [15 empty] | 0 |  |  |  | 0 |  |  | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0
|  |  | 0 | [15 empty] | 0 |  |  |  | 0 |  |  | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0
2J861.1 | Nominal bore 100mm Vent-O-Matt RBX series or similar approved flanged double orifice air release and vacuum break valve | nr | 3 | 92400 | 277200 | [13 empty] | 0 |  |  |  | 0 |  |  | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0
| PAGE TOTAL CARRIED TO COLECTION PAGE |  |  |  | 4946825
BILL 5 - RISING MAIN
ITEM | DESCRIPTION | UNIT | QTY | RATE (KShs) | AMOUNT (KShs)
CLASS K: PIPEWORK - MANHOLES AND PIPEWORK ANCILLARIES
Chambers complete as per the drawings
Air valve Chamber
3K211 | In situ concrete chamber, internal size 1200mm x 1200mm, depth not exceeding 2.0m. (Air Valve chambers) | nr | 3 | 50000 | 150000
Washout Chamber
3K231 | Type 1, depth n.e 2.0m including concrete outfall works | nr | 3 | 100000 | 300000
K6 | Crossings
5K61 | Allow for river crossings, including all couplings, reinforced concrete piers, surrounds, bearings etc. Length n.e 20m | Nr | 1 | 300000 | 300000
2K622.2 | Over-crossing, pipe bore not exceeding 300 -900mm | nr | 1 | 56250 | 56250 | [13 empty] | 0 |  |  |  | 0 |  |  | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0
2K642 | Crossing Hedge, pipe bore not exceeding 300 -900mm | nr | 10 | 6000 | 60000 | [13 empty] | 0 |  |  |  | 0 |  |  | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0
[19 empty] | 0 |  |  |  | 0 |  |  | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0
2K646 | Crossing Fence, pipe bore not exceeding 300 -900mm | nr | 5 | 9000 | 45000 | [13 empty] | 0 |  |  |  | 0 |  |  | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0
2K647 | Crossing existing sewer or drain, pipe bore not exceeding 300 -900mm | nr | 5 | 10000 | 50000 | [13 empty] | 0 |  |  |  | 0 |  |  | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0
2K648 | Crossing existing underground water pipeline size exceeding 50mm, pipe bore not exceeding 300 -900mm | nr | 15 | 10000 | 150000 | [13 empty] | 0 |  |  |  | 0 |  |  | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0
[19 empty] | 0 |  |  |  | 0 |  |  | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0
Micro-tunnelling below bituminous road
Rates quoted shall be deemed to include for costs incurred on traffic control, signage and safety measures during execution of the works.
5K692 | Micro-tunnelling below the bituminous road. Nominal bores 500 mm | m | 20 | 178500 | 3570000
5K694 | Extra over microtunnelling in rock | m3 | 8 | 80000 | 640000 |  | 3.825
Reinstatement
Breaking up, temporary and permanent reinstatement of roads
3K732.1 | Tarmac/paved roads. Pipe nominal bore not exceeding 300-900mm. | m | 20 | 7000 | 140000
3K732.2 | Gravel Roads. Pipe nominal bore not exceeding 300-900mm. | m | 200 | 3000 | 600000
Other Pipework Ancillaries
Supply and erect precast concrete marker post for the following:-
3K820.1 | Pipeline marker post-inscribed 'WM ' | nr | 10.04 | 3000 | 30120
3K820.2 | Air valve marker post-inscribed 'AV' | nr | 3 | 3000 | 9000
3K820.3 | Washout marker post-inscribed 'WO' | nr | 3 | 3000 | 9000
CLASS L: PIPEWORK - SUPPORTS AND PROTECTION, ANCILLARIES TO LAYING AND EXCAVATION
| Excavation of rock as defined in Specifications | [24 empty] | 0 |  |  | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 |  |  | 0
[26 empty] | 0 |  |  | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 |  |  | 0
2L111 | Extras to excavation and backfilling of pipe trenches; Excavation of rock | m3 | 3614.4 | 2500 | 9036000 | [8 empty] | 400 | 1000000 | 0 | 0 | 400 | 1000000 | 760 | 1900000 | 1160 | 2900000 |  | 0 | 1160 | 2900000 |  | 0 | 1160 | 2900000 |  | 0 | 1160 | 2900000 |  | 0 | 1160 | 2900000 |  | 0
2L121 | Extras to excavation and backfilling in chambers; Excavation of rock | m3 | 54 | 2500 | 135000 | [8 empty] | 400 | 1000000 | 0 | 0 | 400 | 1000000 | 760 | 1900000 | 1160 | 2900000 |  | 0 | 1160 | 2900000 |  | 0 | 1160 | 2900000 |  | 0 | 1160 | 2900000 |  | 0 | 1160 | 2900000 |  | 0
| PAGE TOTAL CARRIED TO COLECTION PAGE |  |  |  | 15280370
BILL 5 - RISING MAIN
ITEM | DESCRIPTION | UNIT | QTY | RATE (KShs) | AMOUNT (KShs)
| Bedding and Surround as per Pipeline Standard Details | [17 empty] | 0 |  |  |  | 0 |  |  | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0
[19 empty] | 0 |  |  |  | 0 |  |  | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0
2L522 | Surrounds with excavated selected granular material, pipe bore 500mm | m | 4010 | 505 | 2025050 |  |  | 2000 | 1010000 | 2000 | 1010000 | 5500 | 2777500 | 7500 | 3787500 | 1800 | 909000 | 9300 | 4696500 |  | 0 | 9300 | 4696500 | 0 | 0 | 9300 | 4696500 |  | 0 | 9300 | 4696500 |  | 0 | 9300 | 4696500 |  | 0 | 9300 | 4696500 | 460 | 232300
[19 empty] | 0 |  |  |  | 0 |  |  | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0
2L523-2 | Surrounds with imported granular material, pipe bore 500mm for trench in rock | m | 1000 | 1075 | 1075000 | [10 empty] | 2080 | 2236000 | 2080 | 2236000 | 1680 | 1806000 | 3760 | 4042000 | 2000 | 2150000 | 5760 | 6192000 | 2500 | 2687500 | 8260 | 8879500 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | 0
[19 empty] | 0 |  |  |  | 0 |  |  | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0
2L523-3 | Surrounds with Class C15/20 mass concrete, pipe bore 500mm for road, river and stream crossings | m | 220 | 9750 | 2145000 | [13 empty] | 0 |  |  |  | 0 |  |  | 0 | 0 |  | 0 | 0 | 0 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | 0
Concrete thrust blocks
Thrust blocks - Class 20/20 Mass Concrete, Volume 0.2 - 0.5m3
3L713.2 | For DN 400 11.5o bend volume 0.08 m3 | nr | 7 | 1300 | 9100
3L713.3 | For DN 400 22.5o bend volume 0.24 m3 | nr | 10 | 3700 | 37000
3L713.4 | For DN 400 30o bend volume 0.45 m3 | nr | 7 | 7500 | 52500
3L713.4 | For DN 400 45o bend | nr | 12 | 9000 | 108000
3L713.5 | For DN 400 90o bend volume 1.48 m3 | nr | 16 | 22100 | 353600
Thrust blocks - RC, Class 25/20Volume 0.5 - 1.0m3
3L743 | For 500 x 100 tee | nr | 6 | 9000 | 54000
Anchor blocks on Ruiru River Crossing- RC, Class 25/20 Volume n.e 0.1 m3
3L743 | Anchor blocks including metal strap and holddown bolts | nr |  | 5000 | 0
| Slip anchors on steep sections of the pipe profile as shown on drawings | [17 empty] | 0 |  |  |  | 0 |  |  | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0
[19 empty] | 0 |  |  |  | 0 |  |  | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0
2L834.1 | Slip anchors, height 1.5 - 2.0m, pipe nominal bore 500mm | nr | 5 | 7560 | 37800 | [13 empty] | 0 |  |  |  | 0 |  |  | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0
| PAGE TOTAL CARRIED TO COLECTION PAGE |  |  |  | 5897050
BILL 5 - RISING MAIN
ITEM | DESCRIPTION | UNIT | QTY | RATE (KShs) | AMOUNT (KShs)
BILL 3 Collection Page
| Total Page 1 |  |  |  | 119224050
| Total Page 2 |  |  |  | 4946825
| Total Page 3 |  |  |  | 15280370
| Total Page 4 |  |  |  | 5897050
| BILL 3 COLLECTION CARRIED TO GRAND SUMMARY |  |  |  | 145348295
28953.8436

## BILL NO. 7 - TRANSMISSION MAIN (hidden)
BILL 7 - KATELEMBU TANK- MACHAKOS WATER TRANSMISSION MAINS
ITEM | DESCRIPTION | UNIT | QTY | RATE (KShs) | AMOUNT (KShs)
CLASS A: GENERAL ITEMS
Specified Requirements
Testing of works
Carry out pressure testing, cleansing and sterilising of the pipeline in accordance with clauses 440 and 441 of the specification.
3A260.1 | OD400 HDPE pipe | m | 5210 | 600 | 3126000
CLASS D:DEMOLITION AND SITE CLEARANCE
31260
3D100 | General clearance for pipeline for full width of easement including grubbing out all shrubs etc and removal of all trees of girth < 0.5m | ha | 4 | 200000 | 800000
3D210 | Tree girth 0.5 - 1.0m | nr | 20 | 4000 | 80000
3D220 | Tree girth 1.0 - 2.0m | nr | 15 | 8000 | 120000
3D310 | Tree girth 2.0 - 3.0m | nr | 10 | 12000 | 120000
CLASS I: PIPEWORK - PIPES
| Provide (incl storage and transportation), lay and joint pipes in trench, include for excavation, preparation of surfaces, disposal of excavated material, shoring sides of excavation and backfilling with suitable material | [9 empty] | 0 | 0
[11 empty] | 0 | 0
| Note:- Trench width and minimum cover to pipes is 1m. The cost shall include for strutting, shuttering, stabilizing the earth faces of trenches and keeping the trenches free of water from whatever source by pumping or other means and cost of use of selected soil from the excavated material for compaction in bed and surround to backfilling of trenches, all as specified. | [9 empty] | 0 | 0
| Provide and Lay 'High Density Polyethelyne ' SDR 11 (HDPE PN12.5) | [9 empty] | 0 | 0
2I441.1 | OD 400mm not in trenches | m | 20 | 18560 | 371200 | [12 empty] | 0 |  |  |  | 0 |  |  | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0
|  |  |  | 0 | [13 empty] | 0 |  |  |  | 0 |  |  | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0
2I442.1 | OD 400mm in trenches, depth not exceeding 1.5m | m | 820 | 19260 | 15793200 | [12 empty] | 0 |  |  |  | 0 |  |  | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0
|  |  |  | 0 | [13 empty] | 0 |  |  |  | 0 |  |  | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0
2I443.1 | -Ditto- but depth 1.5m - 2m | m | 950 | 19500 | 18525000 | [5 empty] | 570 | 11115000 | 570 | 11115000 |  | 0 | 570 | 11115000 |  | 0 | 570 | 11115000 |  | 0 | 570 | 11115000 | 500 | 9750000 | 1070 | 20865000 | 970 | 18915000 | 2040 | 39780000 |  | 0 | 2040 | 39780000 |  | 0
|  |  |  | 0 | [7 empty] | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0
2I444.1 | -Ditto- but depth 2.0m - 2.5m | m | 1110 | 19810 | 21989100 | [5 empty] | 1220 | 24168200 | 1220 | 24168200 | 500 | 9905000 | 1720 | 34073200 |  | 0 | 1720 | 34073200 | 1000 | 19810000 | 2720 | 53883200 | 1000 | 19810000 | 3720 | 73693200 |  | 0 | 3720 | 73693200 |  | 0 | 3720 | 73693200 | 95 | 1881950
|  |  |  | 0 | [7 empty] | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0
2I445.1 | -Ditto- but depth 2.5m - 3.0m | m | 1210 | 20310 | 24575100 | [5 empty] | 440 | 8936400 | 440 | 8936400 | 934 | 18969540 | 1374 | 27905940 |  | 0 | 1374 | 27905940 |  | 0 | 1374 | 27905940 |  | 0 | 1374 | 27905940 | 585 | 11881350 | 1959 | 39787290 |  | 0 | 1959 | 39787290 | 85 | 1726350
|  |  |  | 0 | [7 empty] | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0
2I446.1 | -Ditto- but depth 3.0m - 3.5m | m | 760 | 20660 | 15701600 | [5 empty] | 160 | 3305600 | 160 | 3305600 |  | 0 | 160 | 3305600 |  | 0 | 160 | 3305600 |  | 0 | 160 | 3305600 |  | 0 | 160 | 3305600 | 385 | 7954100 | 545 | 11259700 |  | 0 | 545 | 11259700 |  | 0
[13 empty] | 0 |  |  |  | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 |  | 0 |  | 0
2I447.1 | -Ditto- but depth 3.5m - 4.0m | m | 200 | 20360 | 4072000 | [10 empty] | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0
[18 empty] | 0 |  |  |  | 0 |  |  | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0
2I448.1 | -Ditto- but depth exceeding 4m | m | 50 | 20760 | 1038000 | [12 empty] | 0 |  |  |  | 0 |  |  | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0
3I011 | DN 80 in trenches depth n.e 1.5m. | m |  | 600 | 0
3I031 | DN 350 in trenches depth n.e 1.5m. | m |  | 840 | 0
3I032 | Ditto but depth 1.5 - 2m | m |  | 1050 | 0
3I033 | Ditto but depth 2.0 - 2.5m | m |  | 1500 | 0
3I033 | Ditto but depth 2.5 - 3.0 m | m |  | 1800 | 0
| PAGE TOTAL CARRIED TO COLECTION PAGE |  |  |  | 106311200
BILL 7 - KATELEMBU TANK- MACHAKOS WATER TRANSMISSION MAINS
ITEM | DESCRIPTION | UNIT | QTY | RATE (KShs) | AMOUNT (KShs)
3I033 | Ditto but depth 3.0 - 3.5m | m |  | 2100 | 0
CLASS J: PIPEWORK - FITTINGS AND VALVES
All HDPE - PN 12.5 butt fusion fittings unless otherwise indicated. Steel fittings to PN16
Rates to include for provision and fixing. Flanges to PN 10 steel unless otherwise stated
Bends - Short Radius
Single flanged
3J311 | DN 80 GS, 90o | nr |  | 6000 | 0
| Pipeline Horizontal and Vertical Bends | [16 empty] | 0 |  |  |  | 0 |  |  | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0
[18 empty] | 0 |  |  |  | 0 |  |  | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0
2J313.1 | HPDE OD400 11¼o bend | nr | 10 | 21000 | 210000 |  | 34 | 714000 | 34 | 714000 | 70 | 2380 | 104 | 716380 | 22 | 462000 | 126 | 1178380 |  | 0 | 126 | 1178380 |  | 0 | 126 | 1178380 |  | 0 | 126 | 1178380 |  | 0 | 126 | 1178380 |  | 0 | 126 | 1178380 |  | 0
|  |  | 0 | [14 empty] | 0 |  |  |  | 0 |  |  | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0
2J313.2 | Ditto but 22½o bend | nr | 11 | 21000 | 231000 |  | 6 | 126000 | 6 | 126000 | 14 | 84 | 20 | 126084 | 14 | 294000 | 34 | 420084 |  | 0 | 34 | 420084 |  | 0 | 34 | 420084 |  | 0 | 34 | 420084 |  | 0 | 34 | 420084 |  | 0 | 34 | 420084 |  | 0
|  |  | 0 | [14 empty] | 0 |  |  |  | 0 |  |  | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0
2J313.3 | Ditto but 30o bend | nr | 9 | 21000 | 189000 | [12 empty] | 0 |  |  |  | 0 |  |  | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0
|  |  | 0 | [14 empty] | 0 |  |  |  | 0 |  |  | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0
2J313.4 | Ditto but 45o bend | nr | 11 | 30000 | 330000 | [12 empty] | 0 |  |  |  | 0 | 25 | 750000 | 25 | 750000 | 35 | 1050000 | 60 | 1800000 | 18 | 540000 | 78 | 2340000 | 5 | 150000 | 83 | 2490000 | 4 | 120000
|  |  | 0 | [14 empty] | 0 |  |  |  | 0 |  |  | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0
2J313.5 | Ditto but 90o bend | nr | 13 | 35000 | 455000 | [9 empty] | 3 | 105000 | 3 | 105000 | 14 | 490000 | 17 | 595000 | 8 | 280000 | 25 | 875000 | 5 | 175000 | 30 | 1050000 |  | 0 | 30 | 1050000 |  | 0 | 30 | 1050000 | 2 | 70000
Plain ended
3J313.1 | DN 350, 45o | nr |  | 30000 | 0
3J313.2 | DN 350, 30o | nr |  | 21000 | 0
3J313.2 | DN 350, 22.5o | nr |  | 21000 | 0
3J313.3 | DN 350, 11.25o | nr |  | 21000 | 0
| Air Valves and Washouts Fittings | [16 empty] | 0 |  |  |  | 0 |  |  | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0
[18 empty] | 0 |  |  |  | 0 |  |  | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0
| Bends | [16 empty] | 0 |  |  |  | 0 |  |  | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0
[18 empty] | 0 |  |  |  | 0 |  |  | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0
2J311.1 | DN 100 GS, 90o bend (for Type 1 Washouts) | nr | 5 | 11565 | 57825 | [12 empty] | 0 |  |  |  | 0 |  |  | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0
|  |  | 0 | [14 empty] | 0 |  |  |  | 0 |  |  | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0
2J311.2 | Nominal bore 100mm, double flanged long radius 90o bend (for air valves vents) | nr | 4 | 13875 | 55500 | [12 empty] | 0 |  |  |  | 0 |  |  | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0
|  |  | 0 | [14 empty] | 0 |  |  |  | 0 |  |  | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0
| Junctions and Branches |  | 0 | [14 empty] | 0 |  |  |  | 0 |  |  | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0
|  |  | 0 | [14 empty] | 0 |  |  |  | 0 |  |  | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0
2J323.1 | DN 350mm x 100mm plain ended tee with flanged branch tee (for Air Valves) | nr | 4 | 67400 | 269600 |  | 8 | 539200 | 8 | 539200 | 15 | 1011000 | 23 | 1550200 | 12 | 808800 | 35 | 2359000 |  | 0 | 35 | 2359000 |  | 0 | 35 | 2359000 |  | 0 | 35 | 2359000 |  | 0 | 35 | 2359000 |  | 0 | 35 | 2359000 |  | 0
|  |  | 0 | [14 empty] | 0 |  |  |  | 0 |  |  | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0
2J323.2 | DN 350mm x 100mm plain ended tee with flanged branch level invert tee (for Washouts) | nr | 5 | 67400 | 337000 |  | 6 | 404400 | 6 | 404400 | 12 | 808800 | 18 | 1213200 | 8 | 539200 | 26 | 1752400 |  | 0 | 26 | 1752400 |  | 0 | 26 | 1752400 |  | 0 | 26 | 1752400 |  | 0 | 26 | 1752400 |  | 0 | 26 | 1752400 |  | 0
0
| Double Collars as specified |  | 0 | [14 empty] | 0 |  |  |  | 0 |  |  | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0
| Flexible coupling (VJ Type) |  | 0 | [14 empty] | 0 |  |  |  | 0 |  |  | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0
0
2J341.1 | DN 100mm flexible coupling | nr | 5 | 7500 | 37500 | [12 empty] | 0 |  |  |  | 0 |  |  | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0
|  |  | 0 | [14 empty] | 0 |  |  |  | 0 |  |  | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0
2J344.1 | DN 350mm flexible coupling | nr | 18 | 20000 | 360000 | [12 empty] | 0 |  |  |  | 0 |  |  | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0
|  |  | 0 | [14 empty] | 0 |  |  |  | 0 |  |  | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0
| Adaptors |  | 0 | [14 empty] | 0 |  |  |  | 0 |  |  | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0
| Flange adaptors |  | 0 | [14 empty] | 0 |  |  |  | 0 |  |  | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0
0
2J351.1 | DN 100mm flange adaptor | nr | 5 | 4250 | 21250 | [12 empty] | 0 |  |  |  | 0 |  |  | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0
|  |  | 0 | [14 empty] | 0 |  |  |  | 0 |  |  | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0
| Straight Specials as specified |  | 0 | [14 empty] | 0 |  |  |  | 0 |  |  | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0
|  |  | 0 | [14 empty] | 0 |  |  |  | 0 |  |  | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0
2J381.1 | DN100mm diameter socket to spigot piece with thrust flange, 900mm long-WO | nr | 5 | 5085 | 25425 | [12 empty] | 0 |  |  |  | 0 |  |  | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0
|  |  | 0 | [14 empty] | 0 |  |  |  | 0 |  |  | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0
2J381.2 | DN100mm diameter double spigot piece, 15000mm long-WO | nr | 5 | 30520 | 152600 | [12 empty] | 0 |  |  |  | 0 |  |  | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0
0
2J383.1 | DN100mm diameter double flanged riser piece, 2000mm long- Cut to suit-AV | nr | 4 | 16250 | 65000 | [12 empty] | 0 |  |  |  | 0 |  |  | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0
|  |  | 0 | [14 empty] | 0 |  |  |  | 0 |  |  | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0
2J481.1 | Nominal bore 150mm uPVC pipe sleeve over washout valves, 3m long | nr | 5 | 3450 | 17250 | [12 empty] | 0 |  |  |  | 0 |  |  | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0
|  |  | 0 | [14 empty] | 0 |  |  |  | 0 |  |  | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0
| Valves as specified |  | 0 | [14 empty] | 0 |  |  |  | 0 |  |  | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0
|  |  | 0 | [14 empty] | 0 |  |  |  | 0 |  |  | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0
2J811.1 | DN 100mm double flanged isolating Valve (for air valves) | nr | 4 | 42000 | 168000 | [12 empty] | 0 |  |  |  | 0 |  |  | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0
|  |  | 0 | [14 empty] | 0 |  |  |  | 0 |  |  | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0
2J811.2 | DN100mm double flanged Gate Valve (for washouts) | nr | 5 | 45000 | 225000 | [12 empty] | 0 |  |  |  | 0 |  |  | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0
|  |  | 0 | [14 empty] | 0 |  |  |  | 0 |  |  | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0
| Air Valves |  | 0 | [14 empty] | 0 |  |  |  | 0 |  |  | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0
|  |  | 0 | [14 empty] | 0 |  |  |  | 0 |  |  | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0
2J861.1 | DN100mm Vent-O-Matt RBX series or similar approved flanged double orifice air release and vacuum break valve | nr | 4 | 92400 | 369600 | [12 empty] | 0 |  |  |  | 0 |  |  | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0
| PAGE TOTAL CARRIED TO COLECTION PAGE |  |  |  | 3576550
BILL 7 - KATELEMBU TANK- MACHAKOS WATER TRANSMISSION MAINS
ITEM | DESCRIPTION | UNIT | QTY | RATE (KShs) | AMOUNT (KShs)
CLASS K: PIPEWORK - MANHOLES AND PIPEWORK ANCILLARIES
Chambers complete as per the drawings
Air valve Chamber
3K211 | In situ concrete chamber, internal size 1200mm x 1200mm, depth not exceeding 2.0m. (Air Valve chambers) | nr | 4 | 50000 | 200000
Washout Chamber
3K231 | Type 1, depth n.e 2.0m including concrete outfall works | nr | 5 | 100000 | 500000
K6 | Crossings
5K61 | Allow for river crossings, including all couplings, reinforced concrete piers, surrounds, bearings etc. Length n.e 20m | Nr | 1 | 300000 | 300000
2K622.2 | Over-crossing, pipe bore not exceeding 300 -900mm | nr | 1 | 56250 | 56250 | [12 empty] | 0 |  |  |  | 0 |  |  | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0
2K642 | Crossing Hedge, pipe bore not exceeding 300 -900mm | nr | 15 | 6000 | 90000 | [12 empty] | 0 |  |  |  | 0 |  |  | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0
[18 empty] | 0 |  |  |  | 0 |  |  | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0
2K646 | Crossing Fence, pipe bore not exceeding 300 -900mm | nr | 10 | 9000 | 90000 | [12 empty] | 0 |  |  |  | 0 |  |  | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0
2K647 | Crossing existing sewer or drain, pipe bore not exceeding 300 -900mm | nr | 10 | 10000 | 100000 | [12 empty] | 0 |  |  |  | 0 |  |  | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0
2K648 | Crossing existing underground water pipeline size exceeding 50mm, pipe bore not exceeding 300 -900mm | nr | 22 | 10000 | 220000 | [12 empty] | 0 |  |  |  | 0 |  |  | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0
[18 empty] | 0 |  |  |  | 0 |  |  | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0
Micro-tunnelling below bituminous road
Rates quoted shall be deemed to include for costs incurred on traffic control, signage and safety measures during execution of the works.
5K692 | Micro-tunnelling below the bituminous road. Nominal bores 500 mm | m | 20 | 178500 | 3570000
5K694 | Extra over microtunnelling in rock | m3 | 8 | 80000 | 640000 | 3.825
Reinstatement
Breaking up, temporary and permanent reinstatement of roads
3K732.1 | Tarmac/paved roads. Pipe nominal bore not exceeding 300-900mm. | m | 30 | 7000 | 210000
3K732.2 | Gravel Roads. Pipe nominal bore not exceeding 300-900mm. | m | 240 | 3000 | 720000
Other Pipework Ancillaries
Supply and erect precast concrete marker post for the following:-
3K820.1 | Pipeline marker post-inscribed 'WM ' | nr | 10.42 | 3000 | 31260
3K820.2 | Air valve marker post-inscribed 'AV' | nr | 4 | 3000 | 12000
3K820.3 | Washout marker post-inscribed 'WO' | nr | 3 | 3000 | 9000
CLASS L: PIPEWORK - SUPPORTS AND PROTECTION, ANCILLARIES TO LAYING AND EXCAVATION
| Excavation of rock as defined in Specifications | [23 empty] | 0 |  |  | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 |  |  | 0
[25 empty] | 0 |  |  | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 |  |  | 0
2L111 | Extras to excavation and backfilling of pipe trenches; Excavation of rock | m3 | 3751.2 | 2500 | 9378000 | [7 empty] | 400 | 1000000 | 0 | 0 | 400 | 1000000 | 760 | 1900000 | 1160 | 2900000 |  | 0 | 1160 | 2900000 |  | 0 | 1160 | 2900000 |  | 0 | 1160 | 2900000 |  | 0 | 1160 | 2900000 |  | 0
2L121 | Extras to excavation and backfilling in chambers; Excavation of rock | m3 | 81 | 2500 | 202500 | [7 empty] | 400 | 1000000 | 0 | 0 | 400 | 1000000 | 760 | 1900000 | 1160 | 2900000 |  | 0 | 1160 | 2900000 |  | 0 | 1160 | 2900000 |  | 0 | 1160 | 2900000 |  | 0 | 1160 | 2900000 |  | 0
| PAGE TOTAL CARRIED TO COLECTION PAGE |  |  |  | 16329010
BILL 7 - KATELEMBU TANK- MACHAKOS WATER TRANSMISSION MAINS
ITEM | DESCRIPTION | UNIT | QTY | RATE (KShs) | AMOUNT (KShs)
| Bedding and Surround as per Pipeline Standard Details | [16 empty] | 0 |  |  |  | 0 |  |  | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0
[18 empty] | 0 |  |  |  | 0 |  |  | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0
2L522 | Surrounds with excavated selected granular material, pipe bore 500mm | m | 3950 | 505 | 1994750 |  | 2000 | 1010000 | 2000 | 1010000 | 5500 | 2777500 | 7500 | 3787500 | 1800 | 909000 | 9300 | 4696500 |  | 0 | 9300 | 4696500 | 0 | 0 | 9300 | 4696500 |  | 0 | 9300 | 4696500 |  | 0 | 9300 | 4696500 |  | 0 | 9300 | 4696500 | 460 | 232300
[18 empty] | 0 |  |  |  | 0 |  |  | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0
2L523-2 | Surrounds with imported granular material, pipe bore 500mm for trench in rock | m | 1210 | 1075 | 1300750 | [9 empty] | 2080 | 2236000 | 2080 | 2236000 | 1680 | 1806000 | 3760 | 4042000 | 2000 | 2150000 | 5760 | 6192000 | 2500 | 2687500 | 8260 | 8879500 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | 0
[18 empty] | 0 |  |  |  | 0 |  |  | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0
2L523-3 | Surrounds with Class C15/20 mass concrete, pipe bore 500mm for road, river and stream crossings | m | 270 | 9750 | 2632500 | [12 empty] | 0 |  |  |  | 0 |  |  | 0 | 0 |  | 0 | 0 | 0 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | 0
Concrete thrust blocks
Thrust blocks - Class 20/20 Mass Concrete, Volume 0.2 - 0.5m3
3L713.2 | For DN 350 11.5o bend volume 0.08 m3 | nr | 10 | 1300 | 13000
3L713.3 | For DN 350 22.5o bend volume 0.24 m3 | nr | 11 | 3700 | 40700
3L713.4 | For DN 350 30o bend volume 0.45 m3 | nr | 9 | 7500 | 67500
3L713.4 | For DN 350 45o bend | nr | 11 | 9000 | 99000
3L713.5 | For DN 350 90o bend volume 1.48 m3 | nr | 13 | 22100 | 287300
Thrust blocks - RC, Class 25/20Volume 0.5 - 1.0m3
3L743 | For 400 x 100 tee | nr | 9 | 9000 | 81000
Anchor blocks on Ruiru River Crossing- RC, Class 25/20 Volume n.e 0.1 m3
3L743 | Anchor blocks including metal strap and holddown bolts | nr |  | 5000 | 0
| Slip anchors on steep sections of the pipe profile as shown on drawings | [16 empty] | 0 |  |  |  | 0 |  |  | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0
[18 empty] | 0 |  |  |  | 0 |  |  | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0
2L834.1 | Slip anchors, height 1.5 - 2.0m, pipe nominal bore 500mm | nr | 2 | 7560 | 15120 | [12 empty] | 0 |  |  |  | 0 |  |  | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0
| PAGE TOTAL CARRIED TO COLECTION PAGE |  |  |  | 6531620
BILL 7 - KATELEMBU TANK- MACHAKOS WATER TRANSMISSION MAINS
ITEM | DESCRIPTION | UNIT | QTY | RATE (KShs) | AMOUNT (KShs)
BILL 3 Collection Page
| Total Page 1 |  |  |  | 106311200
| Total Page 2 |  |  |  | 3576550
| Total Page 3 |  |  |  | 16329010
| Total Page 4 |  |  |  | 6531620
| BILL 7 COLLECTION CARRIED TO GRAND SUMMARY |  |  |  | 132748380
26443.9004

## BILL NO. 9 -CONSUMER CONNECTION (hidden)
BILL 9 - CONSUMER CONNECTIONS
ITEM NO. | DESCRIPTION | UNIT | QTY | RATE (KShs) | AMOUNT (KShs)
13I | TRENCHING, PIPES AND FITTINGS FOR CONSUMER CONNECTIONS
The following items combine a variety of works such as earthworks, civil works, supplies, mechanical works for pipe laying, testing, destroying of existing pipes, crossing and reinstatement of other underground communications, etc,…All costs are deemed to be included and covered by the unit price!
13I7 | Trenching Pipes and Pipe Laying for Consumers Connection
| Supply and installation of uPVC pipework, including all bends, fittings, specials, warning tapes, testing of pipes as specified, disinfection of pipes; covering also all necessary earthworks such as excavation,backfilling in maximum 30cm layers from/to level 30cm below finished ground level, bedding, compaction and crossings for other underground infrastructure. The item does not cover service valves as listed below, but includes any additional excavation required for these items. Pipe trench dimensions, bedding layers etc, in line with the standard drawings and specifications. | [5 empty] | NUMBER OF CONNECTIONS
| uPVC Pressure Pipe, KS ISO 1452-2: 2009. uPVC PN12.5 unless otherwise stated. | [5 empty] | 37 | 950 | [6 empty] | Total | Round
[12 empty] | 14 m Pipe | Fittings | Exc
13I712.1 | OD 25 | m |  | 6000 | 0 |  |  |  |  | 14 | 37 | 725.2 | 1000 | 4032 | 5757.2 | 6000
13I712.2 | OD 32 | m |  | 8000 | 0 |  |  |  |  | 14 | 58 | 1136.8 | 2000 | 4032 | 7168.8 | 8000
13I712.3 | OD 40 | m |  | 10000 | 0 |  |  |  |  | 14 | 88 | 1724.8 | 4000 | 4032 | 9756.8 | 10000
Taper x2
13I712.4 | OD 50 | m | 4250 | 13000 | 55250000 | 36423 | 37000 |  |  | 14 | 136 | 2665.6 | 6000 | 4032 | 12697.6 | 13000
[6 empty] | 14569.2 | 15000 | 1 | M
13I712.5 | OD 63 | m | 1375 | 18000 | 24750000 | 21853.8 | 22000 |  |  | 14 | 217 | 4253.2 | 9000 | 4032 | 17285.2 | 18000
[7 empty] | 14 | m
9J6 | Pipe saddles or T-pieces | [6 empty] | 1
| Supply and installation of connections to distribution pipe by T-piece or pipe saddles as specified, include for all works and fittings(wherever practicable saddles on larger pipes to be shares by several consumers); for distribution pipe diameter | [5 empty] | 63 mm Fittings | 4500 | 9000
[7 empty] | Pipe % | Adopt | Nr
13J621.1 | OD 63 | Nr |  | 840 | 0 |  | 44.91% | 52 | 2704 | 840 | 850
13J621.2 | On DN 90 | Nr |  | 1340 | 0 |  | 19.07% | 19 | 988 | 1340 | 1400
13J621.3 | On DN 110 | Nr | 255 | 1500 | 382500 |  | 6.835% | 7 | 364 | 1500 | 1500
13J621.4 | Ditto but DN 160 | Nr | 120 | 3750 | 450000 |  | 12% | 12 | 624 | 3750 | 4000
13J621.5 | Ditto but DN 225 | Nr | 232 | 13500 | 3132000 |  | 12.1% | 8 | 416 | 13500 | 13500
13J621.6 | Ditto but DN 355 | Nr | 104 | 24000 | 2496000 |  | 5.089% | 2 | 104 |  | 24000
| PAGE TOTAL CARRIED TO COLECTION PAGE |  |  |  | 86460500
BILL 9 - CONSUMER CONNECTIONS
ITEM NO. | DESCRIPTION | UNIT | QTY | RATE (KShs) | AMOUNT (KShs)
9.3 | Underground water meter chambers
Supply and installation of underground water meter chambers, including all (mechanical and earth!) works, fittings, tappers, valves and other supplies as per standard drawings. The item also including the water meter installation set with water meter substitution pipe but not the meter itself! The chamber suitable for the following water meter size:
9K251.1 | DN 20 | Nr |  | 11000 | 0
9K251.2 | DN 25 | Nr |  | 11000 | 0
9K251.3 | DN 32 | Nr |  | 11000 | 0
9K251.4 | DN 40 | Nr | 355 | 11000 | 3905000
9K251.5 | DN 50 | Nr | 255 | 11000 | 2805000
9K6 | Crossings
9K651 | Allow for crossing existing boundary walls, including reinstatement to original state. Nominal bore not exceeding 200mm (Provisional) | Nr | 352 | 2000 | 704000
9K661 | Allow for crossing existing fences (chain link, barbed wire etc.), including reinstatement to original state. Nominal bore n.e. 200mm (Provisional) | Nr | 250 | 1000 | 250000
9K671 | Allow for crossing existing drains and sewers, and reinstate these after construction of sewer has been completed. Pipe inside diameter n.e. 200mm (Provisional). | Nr | 353 | 2000 | 706000
9K7 | Reinstatement
9K732 | Breaking up, temporary and permanent reinstatement of murram road (Width of road cutting n.e 2m) with 300mm thick well graded stabilised gravel with 3% cement content base compacted using a 8-10 tonne roller to the satisfaction of the Engineer . Nominal bore 300 - 900 mm. Contractor to allow for liason with relevant local authorities and obtaining approval for completed works in his rates. | m | 5280 | 1500 | 7920000 |  |  | 161 | 35
9K732 | Breaking up, temporary and permanent reinstatement of concrete pavements (width of cutting n.e 1 m) with 300mm thick well graded stabilised gravel compacted and concrete layer and finishing to match. Nominal bore n.e 65 mm | m | 1750 | 5000 | 8750000
| PAGE TOTAL CARRIED TO COLECTION PAGE |  |  |  | 25040000
BILL 9 - CONSUMER CONNECTIONS
ITEM NO. | DESCRIPTION | UNIT | QTY | RATE (KShs) | AMOUNT (KShs)
BILL 9 Collection Page
| Total Page 1 |  |  |  | 86460500
| Total Page 2 |  |  |  | 25040000
| BILL 9 COLLECTION CARRIED TO GRAND SUMMARY |  |  |  | 111500500
`

## BILL NO. 8 - DISTRIBUTION LINES (hidden)
BILL 8 - DISTRIBUTION NETWORK
ITEM | DESCRIPTION | UNIT | QTY | RATE (KShs) | AMOUNT (KShs) |  | QTY
CLASS A: GENERAL ITEMS
Specified Requirements
Testing of works
Carry out pressure testing, cleansing and sterilising of the pipeline in accordance with clauses 440 and 441 of the specification.
3A260.1 | Pipe bore n.e 315mm | m | 41960 | 100 | 4196000 |  | 7610
CLASS D:DEMOLITION AND SITE CLEARANCE
clearance shall include demolition and removal of natural and artificial articles, objects and obstructions which are above the original surface. Items for demolition and site clearance shall be deemed to include disposal of materials arising. Items for general clearance include removal of hedges and removal of hedges stumps of any diameter and disposal of materials arising of. Items for removal of trees shall include removal of stumps where required. The girth shall be measured 1m above the ground level. (provisional)
3D100 | General clearance | ha | 8.8116 | 200000 | 1762320 |  | 1.5981
3D210 | Trees of girth 500mm - 1m | nr | 1 | 800 | 800 |  | 1
3D220 | Trees of girth 1 - 2m | nr | 1 | 1000 | 1000 |  | 1
3D310 | Stumps of diameter 150 - 500mm | nr | 1 | 500 | 500 |  | 1
3D320 | Stumps of diameter 500 mm - 1m | nr | 1 | 500 | 500 |  | 1
CLASS I: PIPEWORK - PIPES
Excavate, store, backfill, compact in trench all materials as per trench detail drawings . Rate to include disposal of excess materials as directed by the engineer.
Excavations shall include for strutting. Shuttering, stabilizing excavated surfaces and keeping excavations free of water bailing out, pumping or other means
3I31 | For pipeline in trench depth n.e 1.5m | m | 29372 | 250 | 7343000 |  | 5327
3I43 | Ditto but for depth 1.5– 2.0m | m | 12588 | 350 | 4405800 |  | 2283
3I34 | Excavations in Soft Rock (provisional) | m3 | 4200 |  |  |  | 770
3I45 | Excavations in Hard Rock (provisional) | m3 | 6300 | 3000 | 18900000 |  | 1150
Supply, handle, deliver to site, lay and joint,( rate to include cutting to size, fixing and jointing materials inclusive of sockets, mechanical joints, or rubber rings where applicable). uPVC Pressure Pipe, KS ISO 1452-2: 2009. uPVC PN12.5 unless otherwise stated.
3I011 | DN 355 | m | 0 | 9140 | 0 |  | 740
3I031 | DN 315 | m | 5710 | 7200 | 41112000 |  | 1950
| PAGE TOTAL CARRIED TO COLECTION PAGE |  |  |  | 77721920
BILL 8 - DISTRIBUTION NETWORK
ITEM | DESCRIPTION | UNIT | QTY | RATE (KShs) | AMOUNT (KShs) |  | QTY
3I032 | DN 250 | m | 4100 | 5710 | 23411000 |  | 1810
3I033 | DN 200 | m | 4470 | 4500 | 20115000 |  | 0
3I034 | DN 160 | m | 14080 | 2260 | 31820800 |  | 1030
3I035 | DN 110 | m | 13600 | 1070 | 14552000 |  | 2080
3I036 | DN 63 HDPE PN10 | m | 0 | 380 | 0 |  | 0
CLASS J: PIPEWORK - FITTINGS AND VALVES
Air Valves, Fire Hydrants and Washouts
Supply, handle, deliver to site, fix in place and test inclusive of all fittings, as per drawing No. **** ( rate to exclude construction of chambers).
3J861.1 | For Single small-orifice Air Valve type " Glenfield" or approved equivalent to BS 5163/PN10 with isolating valve on DN 315 pipe | No | 3 | 27000 | 81000 |  | 2
3J861.2 | Ditto 2.22 but on DN 250 pipeline | No | 2 | 27000 | 54000 |  | 2
3J861.3 | Ditto 2.22 but on DN 200 pipeline | No | 3 | 25000 | 75000 |  | 1
3J861.4 | Ditto 2.22 but on DN 160 pipeline | No | 6 | 25000 | 150000 |  | 3
3J861.5 | Ditto 2.22 but on DN 110 pipeline | No | 5 | 25000 | 125000 |  | 3
3J861.6 | For Double orifice Air Valve type "Glenfield" or approved equivalent to BS 5163/PN10 with isolating valve on DN 355 pipe | No | 0 | 30000 | 0 |  | 2
3J862.1 | Washout to detail as shown on drawings | No. | 16 | 30000 | 480000 |  | 11
3J862.2 | Fire Hydrants to BS 750 Type 2 | No. | 3 | 75000 | 225000 |  | 0
TEES
Supply, handle, deliver to site, fix in place and test inclusive of all fittings to details. Include for necessary uPVC-Steel joining fittings. ( rate to exclude gate valves or sluice valves and construction of chambers but include for all other jointing materials and fittings)
3J323.1 | for 350x300 Tees with flanged branch | No | 0 | 50000 | 0 |  | 2
3J323.2 | ditto 2.29 But for 350x100 Tee with flanged branch | No | 0 | 39500 | 0 |  | 2
3J323.3 | ditto 2.29 But for 350x50 Tee with socket branch | No | 0 | 38000 | 0 |  | 2
3J323.4 | For 315x160 Tee with socket branch | No | 2 | 38850 | 77700 |  | 2
3J323.5 | ditto But for 315x 200 Tee with socket branch | No | 4 | 32230 | 128920 |  | 4
3J323.6 | ditto But for 315x110 Tee with socket branch | No | 4 | 30980 | 123920 |  | 2
3J323.7 | ditto But for 315x50 Tee with socket branch | No | 0 | 30980 | 0 |  | 2
3J323.8 | ditto But for 250x160 Tee with socket branch | No | 2 | 29650 | 59300 |  | 2
3J323.9 | ditto But for 200x200 Tee with socket branch | No | 4 | 29650 | 118600 |  | 2
3J323.10 | ditto But for 250x110 Tee with socket branch | No | 5 | 26410 | 132050 |  | 6
3J323.11 | ditto But for 250x50 Tee | No |  | 24880 | 24880 |  | 2
3J323.12 | ditto But for 200x110 Tee | No | 5 | 17920 | 89600 |  | 3
| PAGE TOTAL CARRIED TO COLECTION PAGE |  |  |  | 91843770
BILL 8 - DISTRIBUTION NETWORK
ITEM | DESCRIPTION | UNIT | QTY | RATE (KShs) | AMOUNT (KShs) |  | QTY
3J323.9 | ditto But for 250x110 Tee with socket branch | No | 5 | 28500 | 142500 |  | 7
3J323.13 | ditto But for 200x160 Tee | No | 5 | 16870 | 84350 |  | 1
3J323.14 | ditto But for 160x110 Tee | No |  | 13330 | 13330 |  | 3
3J323.15 | ditto But for 110x110 Tee | No | 3 | 10000 | 30000 |  | 3
Provide for GI-uPVC -To include for all necessary fittings and all works associated with connect to existing GI pipes
3J323.4 | GI-Upvc Tee 200x150 | No | 3 | 49950 | 149850 |  | 2
3J323.5 | ditto But for 160x 150 | No | 4 | 41430 | 165720 |  | 4
3J323.6 | ditto But for 110x150 | No | 4 | 39830 | 159320 |  | 2
Supply, handle, deliver to site, fix in place inclusive of all jointing fittings/accessories and test Sluice valve and gate valve to Tees as shown in drawing No.******. For:
3J811.1 | DN 350 flanged Sluice Valves to BS 5163 type "Glenfield/avk " PN10 or approved equivalent | No | 0 | 70000 | 0 |  | 3
3J811.2 | DN 300 flanged Sluice Valves to BS 5163 type "Glenfield/avk " PN10 or approved equivalent | No | 5 | 50000 | 250000 |  | 4
3J811.3 | DN 250 flanged Sluice Valves to BS 5163 type "Glenfield/avk " PN10 or approved equivalent | No | 3 | 45000 | 135000 |  | 5
3J811.4 | DN 150 flanged Sluice Valves to BS 5163 type "Glenfield/avk " PN10 or approved equivalent | No | 8 | 40000 | 320000 |  | 5
3J811.5 | DN 100 flanged Sluice Valves to BS 5163 type "Glenfield/avk " PN10 or approved equivalent | No | 14 | 37000 | 518000 |  | 14
3J351.1 | Supply, handle, deliver to site, fix in place DN 350 Mechanical joints | No | 0 | 15000 | 0 |  | 18
3J351.2 | Supply, handle, deliver to site, fix in place DN 300 Mechanical joints | No | 30 | 12000 | 360000 |  | 30
3J351.3 | Ditto but for DN 250 Mechanical joints | No | 30 | 10000 | 300000 |  | 44
3J351.4 | Ditto but for DN 200 Mechanical joints | No | 20 | 8000 | 160000 |  | 8
3J351.5 | Ditto but for DN 150 Mechanical joints | No | 20 | 7000 | 140000 |  | 20
3J351.6 | Ditto but for DN 100 Mechanical joints | No | 51 | 6000 | 306000 |  | 56
3J351.8 | Supply, handle, deliver to site, fix in place DN 300 Flanged adaptors | No | 30 | 9000 | 270000 |  | 30
3J351.9 | Ditto but for DN 250 Flanged adaptors | No | 30 | 7000 | 210000 |  | 44
3J351.10 | Ditto but for DN 200 Flanged adaptors | No | 20 | 6000 | 120000 |  | 8
3J351.11 | Ditto but for DN 150 Flanged adaptors | No | 20 | 5500 | 110000 |  | 20
3J351.12 | Ditto but for DN 100 Flanged adaptors | No | 51 | 4500 | 229500 |  | 56
3J351.7 | Supply, handle, deliver to site, fix in place DN 350 Flanged adaptors | No | 0 | 10000 | 0 |  | 18
| PAGE TOTAL CARRIED TO COLECTION PAGE |  |  |  | 4031070
BILL 8 - DISTRIBUTION NETWORK
ITEM | DESCRIPTION | UNIT | QTY | RATE (KShs) | AMOUNT (KShs) |  | QTY
BENDS
Supply, handle, deliver to site, fix in place and test inclusive of all fittings bends as directed by the Engineer. For:
3J313.1 | DN 355 bends | No |  | 43200 | 43200 |  | 3
3J313.2 | DN 315 bends | No | 6 | 30000 | 180000 |  | 5
3J313.2 | DN 250 bends | No | 5 | 18600 | 93000 |  | 6
3J313.3 | DN 200 bends | No | 1 | 15000 | 15000 |  | 1
3J313.3 | DN 160 bends | No | 1 | 10200 | 10200 |  | 1
3J313.4 | DN 110 bends | No | 6 | 6660 | 39960 |  | 2
REDUCERS
3J381.1 | Supply, handling, fixing in place and testing inclusive of all fittings For DN 355x315 reducers |  | 2 | 10200 | 20400 |  | 2
3J381.2 | Ditto but for DN 315x250 | No | 3 | 7680 | 23040 |  | 3
3J381.3 | Ditto but for DN 250x200 | No | 3 | 6000 | 18000 |  | 3
3J381.4 | Ditto but for DN 200x160 | No | 1 | 5160 | 5160 |  | 1
3J381.5 | Ditto but for DN 200x110 | No | 2 | 5160 | 10320 |  | 2
3J381.5 | Ditto but for DN 160x110 | No | 5 | 5160 | 25800 |  | 2
3J381.1 | Supply, handling, fixing in place and testing inclusive of all fittings For HDPE-uPVC OD400x315 reducers/connections | No | 3 | 10200 | 30600 |  | 2
Meters
3J381.6 | Supply and install a DN 315mm dia master meter approved by the Engineer. Rate to include all jointing materials. | No. | 3 | 250000 | 750000 |  | 1
CLASS K: PIPEWORK - MANHOLES AND PIPEWORK ANCILLARIES
Chambers
Supply and deliver materials on site, excavate for a construct complete chambers including precast concrete cover slabs where necessary as shown on the drawing
3K231 | For washout valve sleeve, cap and outfall for washout depth n.e 2.5m as show on drawing No. ***** | No | 16 | 40000 | 640000 |  | 11
3K232 | Ditto as 2.73 but for sluice valves as on drawing No. ***** | No | 60 | 25000 | 1500000 |  | 53
3K233 | Ditto as 2.73 but for Fire hydrants type 2 to BS 750 as on drawing No. ***** | No | 3 | 25000 | 75000 |  | 0
| PAGE TOTAL CARRIED TO COLECTION PAGE |  |  |  | 3479680
BILL 8 - DISTRIBUTION NETWORK
ITEM | DESCRIPTION | UNIT | QTY | RATE (KShs) | AMOUNT (KShs) |  | QTY
Reinstatement
Breaking up, temporary and permanent reinstatement of roads
Include for payment for all statutory fees to the local authorities.
3K732.1 | Tarmac/paved roads. Pipe nominal bore not exceeding 50-400mm. | m | 30 | 7000 | 210000 |  | 30
3K732.2 | Gravel Roads. Pipe nominal bore not exceeding 50-400mm. | m | 240 | 3000 | 720000 |  | 240
Crossings
5K61 | Allow for river crossings, length n.e 20m | Nr | 4 | 300000 | 1200000 |  | 4
Allow for crossing existing drains and sewers, and reinstate these after construction of the water line has been completed.
5K671 | Pipe bore 50mm-400mm | Nr | 50 | 5000 | 250000 |  | 50
2K642 | Crossing Hedge, pipe bore not exceeding 50 -400mm | nr | 25 | 6000 | 150000 |  | 25 | [11 empty] | 0 |  |  |  | 0 |  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[19 empty] | 0 |  |  |  | 0 |  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2K646 | Crossing Fence, pipe bore not exceeding 50 -400mm | nr | 20 | 9000 | 180000 |  | 20 | [11 empty] | 0 |  |  |  | 0 |  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Other Pipework Ancillaries
Pipe markers shall be made from reinforced precast concrete to detail. This item shall be deemed to include supply and fixing the pipe markers and painting as directed by the engineer.
3K820.1 | Pipeline marker post | nr | 119.8857 | 3000 | 359657.1429 |  | 21.7429
3K820.2 | Air valve marker post | nr | 19 | 3000 | 57000 |  | 10
3K820.3 | Washout marker post | nr | 45 | 3000 | 135000 |  | 11
CLASS L: PIPEWORK - SUPPORTS AND PROTECTION, ANCILLARIES TO LAYING AND EXCAVATION
Extra to excavation and backfilling
| Excavation of rock as defined in Specifications | [14 empty] | 0 |  |  | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 |  |  | 0
[16 empty] | 0 |  |  | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 |  |  | 0
2L111 | Extras to excavation and backfilling of pipe trenches; Excavation of rock | m3 | 11750 | 3000 | 35250000 | 0 | 2740 | #REF! | #REF! | 760 | 2280000 | #REF! | #REF! |  | #REF! | #REF! | #REF! |  | 0 | #REF! | #REF! |  | 0 | #REF! | #REF! |  | 0 | #REF! | #REF! |  | 0
2L121 | Extras to excavation and backfilling in chambers; Excavation of rock | m3 | 426.6 | 3000 | 1279800 | 0 | 345.6 | #REF! | #REF! | 760 | 2280000 | #REF! | #REF! |  | #REF! | #REF! | #REF! |  | 0 | #REF! | #REF! |  | 0 | #REF! | #REF! |  | 0 | #REF! | #REF! |  | 0
| Bedding and Surround as per Pipeline Standard Details | [7 empty] | #REF! |  |  |  | #REF! |  |  | 0 | #REF! |  | 0 | 0 | #REF! |  | 0 | 0 | #REF! |  | 0 | 0 | #REF! |  | 0
2L522 | Surrounds with selected granular material, pipe bore n.e 400mm | m | 25176 | 1500 | 37764000 | 1800 | 4566 | #REF! | #REF! |  | #REF! | #REF! | #REF! | 0 | 0 | #REF! | #REF! |  | 0 | #REF! | #REF! |  | 0 | #REF! | #REF! |  | 0 | #REF! | #REF! | 460 | 690000
| PAGE TOTAL CARRIED TO COLECTION PAGE |  |  |  | 77555457.1429
BILL 8 - DISTRIBUTION NETWORK
ITEM | DESCRIPTION | UNIT | QTY | RATE (KShs) | AMOUNT (KShs) |  | QTY
[9 empty] | #REF! |  |  |  | #REF! |  |  | 0 | #REF! |  | 0 | 0 | #REF! |  | 0 | 0 | #REF! |  | 0 | 0 | #REF! |  | 0
2L523-2 | Surrounds with imported granular material, pipe bore n.e 400mm for trench in rock | m | 16784 | 1500 | 25176000 | 2080 | 3044 | #REF! | #REF! | 1680 | 2520000 | #REF! | #REF! | 2000 | 3000000 | #REF! | #REF! | 2500 | 3750000 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | 0
[9 empty] | #REF! |  |  |  | #REF! |  |  | 0 | #REF! |  | 0 | 0 | #REF! |  | 0 | 0 | #REF! |  | 0 | 0 | #REF! |  | 0
2L523-3 | Surrounds with Class C15/20 mass concrete, pipe bore n.e 400mm for road, river and stream crossings | m | 350 | 9750 | 3412500 |  | 350 |  | #REF! |  |  |  | #REF! |  |  | 0 | #REF! |  | 0 | 0 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | 0
Concrete Anchor blocks
3L713.2 | Provide and place mass concrete (1:3:6) for anchor blocks in bends etc Rate to include excavation and necessary formwork (provisional) | m3 | 19 | 15000 | 285000 |  | 18
`
| PAGE TOTAL CARRIED TO COLECTION PAGE |  |  |  | 28873500
BILL 8 - DISTRIBUTION NETWORK
ITEM | DESCRIPTION | UNIT | QTY | RATE (KShs) | AMOUNT (KShs) |  | QTY
BILL COLLECTION
| From page 1 |  |  |  | 77721920
| From page 2 |  |  |  | 91843770
| From page 3 |  |  |  | 4031070
| From page 4 |  |  |  | 3479680
| From page 5 |  |  |  | 28873500
| BILL 3 COLLECTION CARRIED TO GRAND SUMMARY |  |  |  | 205949940
Note on E39: Jackson Nzainga:
Note on E194: losai mgt: New rate . Eng Please check
Note on E228: Jackson Nzainga:

## BILL NO. 3 - RAW WATER (hidden)
BILL No. 3 - RAW WATER MAINS
ITEM NO. | DESCRIPTION | UNIT | QTY | RATE (KShs) | AMOUNT (KShs)
CLASS A - TESTING AND SETTING OUT OF WORKS
Testing pipelines complete including flushing and sterilizing in accordance with the Specificatons
3A360.1 | DN600 and DN 450 steel pipes to 100m maximum test pressure | m | 650 | 100 | 65000 | [25 empty] | 0 |  |  |  | 0 |  |  |  | 0
[17 empty] | 0 |  |  |  | 0 |  |  | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0
3A290 | Set out and prepare construction drawings for the raw water main to include all appurtenant facilities | Item | Sum | 50000 | 50000 |  |  |  |  | 1 | 50000 | 1 | 50000 |  | 0 | 1 | 50000 |  | 0 | 1 | 50000 |  | 0 | 1 | 50000 |  | 0 | 1 | 50000 |  | 0 | 1 | 50000 |  | 0 | 1 | 50000 |  | 0
[17 empty] | 0 |  |  |  | 0 |  |  | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0
| CLASS D - DEMOLITION AND SITE CLEARANCE | [15 empty] | 0 |  |  |  | 0 |  |  | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0
[17 empty] | 0 |  |  |  | 0 |  |  | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0
3D100 | General clearance for pipeline for full width of easement including grubbing out all shrubs etc and removal of all trees of girth < 0.5m | ha | 0.195 | 122000 | 23790 | 0.11111 | 2643.3333 | 0.11111 | 2643.3333 | 0.29 | 6899.1 | 0.40111 | 9542.4333 | 0.15 | 396.5 | 0.55111 | 9938.9333 | 0.1 | 2379 | 0.65111 | 12317.9333 | 0 | 0 | 0.65111 | 12317.9333 | 0.1 | 6538.98 | 0.75111 | 18856.9133 | 0.1 | 2379 | 0.85111 | 21235.9133 | 0.1 | 12200 | 0.95111 | 33435.9133 |  | 0
[17 empty] | 0 |  |  |  | 0 |  |  | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0
| Cutting of trees, removal and disposal of stumps with hole backfilled with suitable material from excavated pipe trench | [15 empty] | 0 |  |  |  | 0 |  |  | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0
[17 empty] | 0 |  |  |  | 0 |  |  | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0
3D210 | Tree girth 0.5 - 1.0m | nr | 3 | 500 | 1500 | 23 | 11500 | 23 | 11500 | 53 | 26500 | 76 | 38000 |  | 0 | 76 | 38000 |  | 0 | 76 | 38000 |  | 0 | 76 | 38000 | 120 | 60000 | 196 | 98000 |  | 0 | 196 | 98000 |  | 0 | 196 | 98000 |  | 0
[7 empty] | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0
3D220 | Tree girth 1.0 - 2.0m | nr | 1 | 750 | 750 | 8 | 6000 | 8 | 6000 | 60 | 45000 | 68 | 51000 |  | 0 | 68 | 51000 |  | 0 | 68 | 51000 |  | 0 | 68 | 51000 | 80 | 60000 | 148 | 111000 |  | 0 | 148 | 111000 |  | 0 | 148 | 111000 |  | 0
[17 empty] | 0 |  |  |  | 0 |  |  | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0
| CLASS I - PIPEWORK - PIPES | [15 empty] | 0 |  |  |  | 0 |  |  | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0
[17 empty] | 0 |  |  |  | 0 |  |  | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0
| PN10 Steel Pipes, cement mortar lined and epoxy coated socket to spigot with rubber ring jointed to Clause 408: Supply and transport pipes, break out surface, excavate trench, cut and lay pipes, backfill with selected material from the trench excavations and compact, disposal of surplus all as specified. | [15 empty] | 0 |  |  |  | 0 |  |  | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0
[17 empty] | 0 |  |  |  | 0 |  |  | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0
3I441.1 | Nominal bore 600mm not in trenches | m | 30 | 17465 | 523950 |  |  |  |  | 600 | 17465 | [5 empty] | 0 |  |  |  | 0 |  |  | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0.1
[10 empty] | 450 | 13098.75 | [5 empty] | 0 |  |  |  | 0 |  |  | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0
3I442.1 | Nominal bore 600mm in trenches, depth not exceeding 1.5m | m | 180 | 18100 | 3258000 | [11 empty] | 0 |  |  |  | 0 |  |  | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0.6
[17 empty] | 0 |  |  |  | 0 |  |  | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0
3I443.1 | -Ditto- but depth 1.5m - 3m | m | 90 | 18405 | 1656450 |  |  |  |  | 570 | 10490850 | 570 | 10490850 |  | 0 | 570 | 10490850 |  | 0 | 570 | 10490850 |  | 0 | 570 | 10490850 | 500 | 9202500 | 1070 | 19693350 | 970 | 17852850 | 2040 | 37546200 |  | 0 | 2040 | 37546200 |  | 0 | 0.3
[7 empty] | 650 |  | 5438400 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0
3I444.1 | Nominal bore 450mm not in trenches | m | 35 | 11840 | 414400
3145.1 | Nominal bore 450mm in trenches, depth not exceeding 1.5m | m | 210 | 12050 | 2530500
3146.1 | -Ditto- but depth 1.5m - 3m | m | 105 | 13000 | 1365000
| CLASS J - PIPEWORK - FITTINGS AND VALVES | [15 empty] | 0 |  |  |  | 0 |  |  | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0
[17 empty] | 0 |  |  |  | 0 |  |  | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0
| All steel fittings to be Epoxy Coated and Lined. Flanges to NP10 for all fittings and valves | [15 empty] | 0 |  |  |  | 0 |  |  | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0
PAGE TOTAL CARRIED TO BILL 3.0 COLLECTION SHEET |  |  |  |  | 9889340 | 400 | 21000
[6 empty] | 450 | 23625 | 11.25
[7 empty] | 46725 | 22.25
BILL No. 3 - RAW WATER MAINS
ITEM NO. | DESCRIPTION | UNIT | QTY | RATE (KShs) | AMOUNT (KShs)
| Pipeline Horizontal and Vertical Bends | [15 empty] | 0 |  |  |  | 0 |  |  | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0
3J313.1 | Nominal bore 600mm double sockettted 11¼o bend | nr | 1 | 54845 | 54845 | 34 | 1864730 | 34 | 1864730 | 70 | 2380 | 104 | 1867110 | 22 | 1206590 | 126 | 3073700 |  | 0 | 126 | 3073700 |  | 0 | 126 | 3073700 |  | 0 | 126 | 3073700 |  | 0 | 126 | 3073700 |  | 0 | 126 | 3073700 |  | 0
3J313.2 | Nominal bore 450mm double sockettted 11¼o bend | nr | 2 | 23625 | 47250 | [11 empty] | 0 |  |  |  | 0 |  |  | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0
3J313.3 | Nominal bore 600mm double socketted 22½o bend | nr | 3 | 60350 | 181050 | 6 | 362100 | 6 | 362100 | 14 | 84 | 20 | 362184 | 14 | 844900 | 34 | 1207084 |  | 0 | 34 | 1207084 |  | 0 | 34 | 1207084 |  | 0 | 34 | 1207084 |  | 0 | 34 | 1207084 |  | 0 | 34 | 1207084 |  | 0
0
3J313.4 | Nominal bore 450mm double socketted 22½o bend | nr | 3 | 26625 | 79875
[17 empty] | 0 |  |  |  | 0 |  |  | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0
3J313.3 | Nominal bore 600mm double socketted 45o bend | nr | 3 | 73000 | 219000 | [11 empty] | 0 |  |  |  | 0 | 25 | 1825000 | 25 | 1825000 | 35 | 2555000 | 60 | 4380000 | 18 | 1314000 | 78 | 5694000 | 5 | 365000 | 83 | 6059000 | 4 | 292000
[5 empty] | 0 | [11 empty] | 0 |  |  |  | 0 |  |  | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0
| Nominal bore 450mm double socketted 45o bend | nr | 3 | 30000 | 90000
0
3J313.4 | Nominal bore 600mm double socketted 90o bend | nr | 1 | 80300 | 80300 | [8 empty] | 3 | 240900 | 3 | 240900 | 14 | 1124200 | 17 | 1365100 | 8 | 642400 | 25 | 2007500 | 5 | 401500 | 30 | 2409000 |  | 0 | 30 | 2409000 |  | 0 | 30 | 2409000 | 2 | 160600
0
3J313.5 | Nominal bore 450mm double socketted 90o bend | nr | 1 | 40000 | 40000
Air Valves and Washouts Fittings
| Bends (NP10) | [15 empty] | 0 |  |  |  | 0 |  |  | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0
[17 empty] | 0 |  |  |  | 0 |  |  | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0
3J311.1 | Nominal bore 100mm, flanged plain ended 90o bend (for Type 1 Washouts) | nr | 1 | 11565 | 11565 | [11 empty] | 0 |  |  |  | 0 |  |  | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0
|  |  | 0 | [13 empty] | 0 |  |  |  | 0 |  |  | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0
2J311.2 | Nominal bore 100mm, double flanged long radius 90o bend (for air valves vents) | nr | 1 | 13875 | 13875 | [11 empty] | 0 |  |  |  | 0 |  |  | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0
|  |  | 0 | [13 empty] | 0 |  |  |  | 0 |  |  | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0
| Junctions and Branches (NP10) |  | 0 | [13 empty] | 0 |  |  |  | 0 |  |  | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0
|  |  | 0 | [13 empty] | 0 |  |  |  | 0 |  |  | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0
3J323.1 | Nominal bore 500mm x 100mm double socket tee with flanged branch tee (for Air Valves) | nr | 1 | 67400 | 67400 | 8 | 539200 | 8 | 539200 | 15 | 1011000 | 23 | 1550200 | 12 | 808800 | 35 | 2359000 |  | 0 | 35 | 2359000 |  | 0 | 35 | 2359000 |  | 0 | 35 | 2359000 |  | 0 | 35 | 2359000 |  | 0 | 35 | 2359000 |  | 0
|  |  | 0 | [13 empty] | 0 |  |  |  | 0 |  |  | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0
3J323.2 | Nominal bore 500mm x 100mm double socket with flanged branch level invert tee (for Washouts) | nr | 1 | 67400 | 67400 | 6 | 404400 | 6 | 404400 | 12 | 808800 | 18 | 1213200 | 8 | 539200 | 26 | 1752400 |  | 0 | 26 | 1752400 |  | 0 | 26 | 1752400 |  | 0 | 26 | 1752400 |  | 0 | 26 | 1752400 |  | 0 | 26 | 1752400 |  | 0
0
| Double Collars to PN10 as specified |  | 0 | [13 empty] | 0 |  |  |  | 0 |  |  | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0
|  |  | 0 | [13 empty] | 0 |  |  |  | 0 |  |  | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0
3J341.1 | Nominal bore 100mm flexible coupling | nr | 1 | 5385 | 5385 | [11 empty] | 0 |  |  |  | 0 |  |  | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0
|  |  | 0 | [13 empty] | 0 |  |  |  | 0 |  |  | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0
3J344.1 | Nominal bore 600mm flexible coupling | nr | 2 | 31765 | 63530 | [11 empty] | 0 |  |  |  | 0 |  |  | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0
0
3J345.1 | Nominal bore 450mm flexible coupling | nr | 2 | 20000 | 40000 | [11 empty] | 0 |  |  |  | 0 |  |  | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0
| Adaptors (NP10) | [15 empty] | 0 |  |  |  | 0 |  |  | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0
[17 empty] | 0 |  |  |  | 0 |  |  | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0
3J351.1 | Nominal bore 100mm flange adaptor | nr | 1 | 4250 | 4250 | [11 empty] | 0 |  |  |  | 0 |  |  | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0
[17 empty] | 0 |  |  |  | 0 |  |  | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0
| Straight Specials to PN10 Pressure as specified | [15 empty] | 0 |  |  |  | 0 |  |  | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0
[17 empty] | 0 |  |  |  | 0 |  |  | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0
3J381.1 | Nominal bore 100mm diameter socket to spigot piece with thrust flange, 900mm long-WO | nr | 1 | 5085 | 5085 | [11 empty] | 0 |  |  |  | 0 |  |  | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0
[17 empty] | 0 |  |  |  | 0 |  |  | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0
3J381.2 | Nominal bore 100mm diameter double spigot piece, 15000mm long-WO | nr | 1 | 30520 | 30520 | [11 empty] | 0 |  |  |  | 0 |  |  | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0
3J383.1 | Nominal bore 100mm diameter double flanged riser piece, 2000mm long- Cut to suit-AV | nr | 1 | 16250 | 16250 | [11 empty] | 0 |  |  |  | 0 |  |  | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0
PAGE TOTAL CARRIED TO BILL 3.0 COLLECTION SHEET |  |  |  |  | 1117580
BILL No. 3 - RAW WATER MAINS
ITEM NO. | DESCRIPTION | UNIT | QTY | RATE (KShs) | AMOUNT (KShs)
|  |  | 0 | [13 empty] | 0 |  |  |  | 0 |  |  | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0
3J481.1 | Nominal bore 150mm uPVC pipe sleeve over washout valves, 3m long | nr | 1 | 3450 | 3450
Valves to PN 10 Pressure as specified
|  |  | 0 | [13 empty] | 0 |  |  |  | 0 |  |  | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0
3J811.1 | Nominal bore 100mm double flanged isolating Valve (for air valves) | nr | 1 | 42000 | 42000 | [11 empty] | 0 |  |  |  | 0 |  |  | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0
|  |  | 0 | [13 empty] | 0 |  |  |  | 0 |  |  | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0
3J811.2 | Nominal bore 100mm double flanged Gate Valve (for washouts) | nr | 1 | 45000 | 45000 | [11 empty] | 0 |  |  |  | 0 |  |  | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0
|  |  | 0 | [13 empty] | 0 |  |  |  | 0 |  |  | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0
| Air Valves to PN 10 Pressure as specified |  | 0 | [13 empty] | 0 |  |  |  | 0 |  |  | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0
|  |  | 0 | [13 empty] | 0 |  |  |  | 0 |  |  | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0
3J861.1 | Nominal bore 100mm Vent-O-Matt RBX series or similar approved flanged double orifice air release and vacuum break valve | nr | 1 | 92400 | 92400 | [11 empty] | 0 |  |  |  | 0 |  |  | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0
| Line Valves | [15 empty] | 0 |  |  |  | 0 |  |  | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0
[17 empty] | 0 |  |  |  | 0 |  |  | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0
Rate to include supply and installation of Valves with all fittings (Flanged Tee, pipe pieces, valve, Mechanical joints, couplings) as per standard drawing. Rate exclusive of Manhole
[17 empty] | 0 |  |  |  | 0 |  |  | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0
3J843.1 | DN 600 Butterfly Valve | nr | 1 | 11565 | 11565 | [11 empty] | 0 |  |  |  | 0 |  |  | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0
VJ Couplings
[17 empty] | 0 |  |  |  | 0 |  |  | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0
2J344.1 | Nominal bore 600mm flexible coupling | nr | 10 | 31765 | 317650 | [11 empty] | 0 |  |  |  | 0 |  |  | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0
[17 empty] | 0 |  |  |  | 0 |  |  | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0
| Straight Specials to PN10 Pressure as specified | [15 empty] | 0 |  |  |  | 0 |  |  | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0
[17 empty] | 0 |  |  |  | 0 |  |  | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0
2J381.10 | Nominal bore 600mm diameter flanged spigot pipe, 1200mm long | nr | 2 | 5085 | 10170 | [11 empty] | 0 |  |  |  | 0 |  |  | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0
| CLASS K - PIPEWORK - MANHOLES AND PIPEWORK ANCILLARIES | [15 empty] | 0 |  |  |  | 0 |  |  | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0
[17 empty] | 0 |  |  |  | 0 |  |  | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0
| Chambers complete as per the drawings. Rate to include lockable HDPE covers. | [15 empty] | 0 |  |  |  | 0 |  |  | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0
[17 empty] | 0 |  |  |  | 0 |  |  | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0
2K233.1 | In situ concrete chamber, internal size 1200mm x 1200mm, depth not exceeding 2.0m. (Air Valve chambers) | nr | 1 | 30000 | 30000 | [9 empty] | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0
2K233.2 | In situ concrete chamber, internal size 1400mm x 1400mm, depth not exceeding 2.0m. (Washout Valve chambers) | nr | 1 | 40000 | 40000
[17 empty] | 0 |  |  |  | 0 |  |  | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0
2K236.3 | In situ concrete chamber, internal size 1800mm x 1800mm, depth not exceeding 4.0m for line valve chambers and Interconnection | nr | 1 | 60000 | 60000 | [11 empty] | 0 |  |  |  | 0 |  |  | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0
PAGE TOTAL CARRIED TO BILL 3.0 COLLECTION SHEET |  |  |  |  | 652235
BILL No. 3 - RAW WATER MAINS
ITEM NO. | DESCRIPTION | UNIT | QTY | RATE (KShs) | AMOUNT (KShs)
| Crossings | [15 empty] | 0 |  |  |  | 0 |  |  | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0
[17 empty] | 0 |  |  |  | 0 |  |  | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0
| River crossings, width not exceeding 20m, including all couplings, reinforced concrete piers, surrounds, bearings etc as per standard drawings | [15 empty] | 0 |  |  |  | 0 |  |  | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0
[17 empty] | 0 |  |  |  | 0 |  |  | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0
2K622.2 | Over-crossing, pipe bore not exceeding 300 -900mm | nr | 1 | 56250 | 56250 | [11 empty] | 0 |  |  |  | 0 |  |  | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0
| Pipeline Marker Posts | [15 empty] | 0 |  |  |  | 0 |  |  | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0
[17 empty] | 0 |  |  |  | 0 |  |  | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0
2K820.1 | Marker post for Line Valve inscribed 'LV' | nr | 1 | 2000 | 2000 | [11 empty] | 0 |  |  |  | 0 |  |  | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0
[17 empty] | 0 |  |  |  | 0 |  |  | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0
2K820.2 | -Ditto- but Air Valve inscribed 'AV' | nr | 1 | 2000 | 2000 | [11 empty] | 0 |  |  |  | 0 |  |  | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0
2K820.3 | -Ditto- but Water Main inscribed 'WM ' | nr | 6 | 2000 | 12000 | [11 empty] | 0 |  |  |  | 0 |  |  | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0
[17 empty] | 0 |  |  |  | 0 |  |  | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0
2K820.4 | -Ditto- but Wash Out inscribed 'WO' | nr | 1 | 2000 | 2000 | [11 empty] | 0 |  |  |  | 0 |  |  | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0
| CLASS L - PIPEWORK SUPPORTS AND PROTECTION, ANCILLARIES TO LAYING AND EXCAVATION | [15 empty] | 0 |  |  |  | 0 |  |  | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0
| Excavation of rock as defined in Specifications | [22 empty] | 0 |  |  | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 |  |  | 0
[24 empty] | 0 |  |  | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 |  |  | 0
2L111 | Extras to excavation and backfilling of pipe trenches; Excavation of rock | m3 | 195 | 1200 | 234000 | [6 empty] | 400 | 480000 | 0 | 0 | 400 | 480000 | 760 | 912000 | 1160 | 1392000 |  | 0 | 1160 | 1392000 |  | 0 | 1160 | 1392000 |  | 0 | 1160 | 1392000 |  | 0 | 1160 | 1392000 |  | 0
2L121 | Extras to excavation and backfilling in chambers; Excavation of rock | m3 | 9.72 | 1200 | 11664 | [6 empty] | 400 | 480000 | 0 | 0 | 400 | 480000 | 760 | 912000 | 1160 | 1392000 |  | 0 | 1160 | 1392000 |  | 0 | 1160 | 1392000 |  | 0 | 1160 | 1392000 |  | 0 | 1160 | 1392000 |  | 0
| Bedding and Surround as per Pipeline Standard Details | [15 empty] | 0 |  |  |  | 0 |  |  | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0
[17 empty] | 0 |  |  |  | 0 |  |  | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0
2L522 | Surrounds with excavated selected granular material, pipe bore < 600mm, | m | 350 | 505 | 176750 | 2000 | 1010000 | 2000 | 1010000 | 5500 | 2777500 | 7500 | 3787500 | 1800 | 909000 | 9300 | 4696500 |  | 0 | 9300 | 4696500 | 0 | 0 | 9300 | 4696500 |  | 0 | 9300 | 4696500 |  | 0 | 9300 | 4696500 |  | 0 | 9300 | 4696500 | 460 | 232300
[17 empty] | 0 |  |  |  | 0 |  |  | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0
2L523-2 | Surrounds with imported granular material, pipe bore < 600mm for trench in rock | m | 300 | 1075 | 322500 | [8 empty] | 2080 | 2236000 | 2080 | 2236000 | 1680 | 1806000 | 3760 | 4042000 | 2000 | 2150000 | 5760 | 6192000 | 2500 | 2687500 | 8260 | 8879500 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | 0
[17 empty] | 0 |  |  |  | 0 |  |  | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0
| Thrust blocks for bends, tees, blank ends and anchor blocks for tapers, gate valves and vertical bends. | [11 empty] | 0 |  |  |  | 0 |  |  |  | 0 |  |  | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0
[13 empty] | 0 |  |  |  | 0 |  |  |  | 0 |  |  | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0
2L723 | Concrete thrust and anchor blocks, volume 0.2- 0.5m3, pipe nominal bore < 600mm | nr | 2 | 7875 | 15750 | 40 | 315000 | 40 | 315000 | 70 | 551250 | 110 | 866250 | 47 | 370125 | 157 | 1236375 |  | 0 | 157 | 1236375 |  | 0 | 157 | 1236375 |  | 0 | 157 | 1236375 |  | 0 | 157 | 1236375 |  | 0 | 157 | 1236375 |  | 0 | total valves | 16
[40 empty] | total bends | 3
2L724 | Concrete thrust and anchor blocks, volume 0.5- 1.0 m3, pipe nominal bore < 600mm | nr | 3 | 16875 | 50625 | [7 empty] | 0 | 15 | 253125 | 15 | 253125 | 35 | 590625 | 50 | 843750 | 35 | 590625 | 85 | 1434375 | 65 | 1096875 | 150 | 2531250 | 30 | 506250 | 180 | 3037500 | 15 | 253125 | 195 | 3290625 |  | 0
[13 empty] | 0 |  |  |  | 0 |  |  |  | 0 |  |  | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0
2L725 | Concrete thrust and anchor blocks, volume 1.0 - 2.0 m3, pipe nominal bore < 600mm | nr | 10 | 33750 | 337500 | [7 empty] | 0 |  |  |  | 0 |  |  |  | 0 |  |  | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 | 45 | 1518750 | 45 | 1518750 | 18 | 607500
[13 empty] | 0 |  |  |  | 0 |  |  |  | 0 |  |  | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0
2L726 | Concrete thrust and anchor blocks, volume 2.0 - 4.0 m3, pipe nominal bore < 600mm | nr | 2 | 67500 | 135000 |  |  |  |  | 32 | 2160000 | 32 | 2160000 | 12 | 810000 | 44 | 2970000 |  | 0 | 44 | 2970000 | 23 | 1552500 | 67 | 4522500 | 58 | 3915000 | 125 | 8437500 | 50 | 3375000 | 175 | 11812500 | 18 | 1215000 | 193 | 13027500 |  | 0
| Slip anchors on steep sections of the pipe profile as shown on Standard drawing | [15 empty] | 0 |  |  |  | 0 |  |  | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0
PAGE TOTAL CARRIED TO BILL 3.0 COLLECTION SHEET |  |  |  |  | 1358039
BILL No. 3 - RAW WATER MAINS
ITEM NO. | DESCRIPTION | UNIT | QTY | RATE (KShs) | AMOUNT (KShs)
[17 empty] | 0 |  |  |  | 0 |  |  | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0
2L834.1 | Slip anchors, height 1.5 - 2.0m, pipe nominal bore < 600mm | nr | 10 | 7560 | 75600 | [11 empty] | 0 |  |  |  | 0 |  |  | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0
| CLASS N - MISCELLENEOUS METALWORK | [15 empty] | 0 |  |  |  | 0 |  |  | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0
[17 empty] | 0 |  |  |  | 0 |  |  | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0
2N130.1 | Supply and install a 20 m Steel Bridge across River Maruba to facilitate crossing to/from the Intake works. The Bridge to be anchored on RC piers and Steel I-section bridge deck. The floor surface shall be checkered plates and with suitable handrails. | Nr | 1 | 300000 | 300000 | [11 empty] | 0 |  |  |  | 0 |  |  | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0
[8 empty] | 2 | 3000
| Erosion Control Measures as shown on Drawing | [6 empty] | 100 | 150000 | [7 empty] | 0 |  |  |  | 0 |  |  | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0
[6 empty] | 45000 | 480 | [9 empty] | 0 |  |  |  | 0 |  |  | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0
2X420.1 | Additional rock filled gabion mattress; 0.5m thickness | m2 | 200 | 1000 | 200000 |  | 100 | 1 | 1500 | [7 empty] | 0 |  |  |  | 0 |  |  | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 |  |  | 200m stretch
[8 empty] | 100 | 150000 | 195000 | [6 empty] | 0 |  |  |  | 0 |  |  | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0
2X900.1 | Channel Type A with surface compacted and planted with Napier grass or other specified grass | m | 450 | 1500 | 675000 | [11 empty] | 0 |  |  |  | 0 |  |  | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0
PAGE TOTAL CARRIED TO BILL 3.0 COLLECTION SHEET |  |  |  |  | 1250600
BILL No. 3 - RAW WATER MAINS
ITEM NO. | DESCRIPTION |  |  |  | AMOUNT (KShs)
BILL No. 3 COLLECTION
| PAGE 12 TOTAL |  |  |  | 9889340
| PAGE 13 TOTAL |  |  |  | 1117580
| PAGE 14 TOTAL |  |  |  | 652235
| PAGE 15 TOTAL |  |  |  | 1358039
| PAGE 16 TOTAL |  |  |  | 1250600
| BILL 3.0 COLLECTION CARRIED TO GRAND SUMMARY |  |  |  | 14267794

## Bill No. 2 - Rising Main
BILL 2 - SECOND BARICHO - KAKUYUNI RISING MAIN
ITEM | DESCRIPTION | UNIT | QTY | RATE (KShs) | AMOUNT (KShs)
CLASS A: GENERAL ITEMS
Specified Requirements
A25 | Testing of works
Pipeline testing and commissioning for the whole works, including all necessary equipment, materials and works necessary for testing, such as thrust blocks, anchor blocks, transportation and use of water, pipe fittings, disposal of used water.
A251 | DN 800mm Steel pipes, PN16 | m | 29350 |  | 0
Disinfection of Pipe lines: Flushing with clear water, filling with water containing 0.05 g/l calcium hypochlorite, left for 24 hours. This includes supply of all necessary equipment, materials, chemicals and water, measurement of residual chlorine, all as specified and safe disposal of disinfecting water to Engineer's approval.
A252 | DN 800mm Steel Pipes | m | 29350 |  | 0
CLASS D:DEMOLITION AND SITE CLEARANCE
D100 | General site clearance for pipeline for full width of easement including grubbing out all shrubs etc and removal of all trees of girth < 0.5m | ha | 5.8 |  | 0
D210 | Tree girth 0.5 - 1.0m | nr | 100 |  | 0
D220 | Tree girth 1.0 - 2.0m | nr | 75 |  | 0
D310 | Tree girth 2.0 - 3.0m | nr | 25 |  | 0
CLASS I: PIPEWORK - PIPES
This Bill Only Covers Rates for Procurement of Pipes and Associated Fittings, Transport to Contractor's Site Store and Storage. Including Supply of Jointing materials, couplings, Bolts, Nuts etc.
Steel Pipes - Joints as stated
PN16 Steel Pipes, epoxy lined, epoxy coated with polyethylene coating Pushfit Socket and Spigot Joints and couplings where necessary with rubber gaskets
I43 | DN 800 PN 16 | m | 29350 |  | 0
Transport the procured pipes to site, break out surface, excavate trench, cut and lay pipes, backfill with selected material from the trench excavations and compact, disposal of surplus all as specified, shoring Sides of Excavation trenches, Backfilling and final Reinstatement.
I441.1 | Nominal bore 900mm in trenches, depth not exceeding 1.5m | m | 1468 |  | 0 | [10 empty] | 0 | 0 | 0 |  | 0
[16 empty] | 0 | 0 | 0 |  | 0
I442.1 | Ditto - but depth 1.5m - 2m | m | 23480 |  | 0 | [10 empty] | 0 | 0 | 0 |  | 0
PAGE TOTAL CARRIED TO COLECTION PAGE
[16 empty] | 0 | 0 | 0 |  | 0
I443.1 | Ditto - but depth exceeding 2m | m | 4403 |  | 0 | [10 empty] | 0 | 0 | 0 |  | 0
I444 | Flanged steel pipes, Nominal Bore 250mm in trenches (for washouts)
1444.1 | Depth 1.5m - 2.5m | m | 35 |  | 0
I445 | uPVC Socket and Spigot Pipes
uPVC Class "B" Socket and Spigot pipes for draining of chambers: Nominal Bore - 160mm in trenches
I445.1 | Depth 2.0m - 2.5m | m | 60 |  | 0
I445.2 | Depth 2.5m - 3.0m | m | 60 |  | 0
[16 empty] | 0 | 0 | 0 |  | 0
CLASS J: PIPEWORK - FITTINGS AND VALVES
Transport from Site Store, Lay and Joint Pipe Fittings in Trench, Include for Excavation, Preparation of Surfaces, Disposal of Excavated Material, Shoring Sides of Excavation and Backfilling.
The steel fittings shall be Epoxy Coated and Lined, a mix of Push fit, plain ended and flanged. Flanges to NP20 for all fittings and valves
Rates to include for provision and fixing. Flanges to NP20 steel unless otherwise stated
| Pipeline Horizontal and Vertical Bends - Push fit | [14 empty] | 0 | 0 | 0 |  | 0
[16 empty] | 0 | 0 | 0 |  | 0
J313.1 | Nominal bore 800mm 11¼o bend | nr | 15 |  | 0 | [10 empty] | 0 | 0 | 0 |  | 0
[16 empty] | 0 | 0 | 0 |  | 0
J313.2 | Nominal bore 800mm 22½o bend | nr | 20 |  | 0 | [10 empty] | 0 | 0 | 0 |  | 0
[16 empty] | 0 | 0 | 0 |  | 0
J313.4 | Nominal bore 800mm 45o bend | nr | 12 |  | 0 | [10 empty] | 0 | 0 | 0 | 4 | 0
[16 empty] | 0 | 0 | 0 |  | 0
J313.5 | Nominal bore 800mm 90o bend | nr | 10 |  | 0 | [10 empty] | 0 | 0 | 0 | 2 | 0
Pipeline Horizontal and vertical Bends - All flanged (Provisional)
J313.6 | Nominal Bore 800mm (11¼o, 22½o, 45o & 90o) | nr | 15 |  | 0
PAGE TOTAL CARRIED TO COLECTION PAGE
| Air Valves and Washouts Fittings | [14 empty] | 0 | 0 | 0 |  | 0
[16 empty] | 0 | 0 | 0 |  | 0
| Bends (NP20) | [14 empty] | 0 | 0 | 0 |  | 0
[16 empty] | 0 | 0 | 0 |  | 0
J311.1 | Nominal bore 250mm, flanged plain ended 90o bend (for Type 1 Washouts) | nr | 7 |  | 0 | [10 empty] | 0 | 0 | 0 |  | 0
[16 empty] | 0 | 0 | 0 |  | 0
J311.2 | Nominal bore 200mm, double flanged long radius 90o bend (for air valves vents) | nr | 32 |  | 0 | [10 empty] | 0 | 0 | 0 |  | 0
[16 empty] | 0 | 0 | 0 |  | 0
| Junctions and Branches (NP20) | [14 empty] | 0 | 0 | 0 |  | 0
[16 empty] | 0 | 0 | 0 |  | 0
J323.1 | Nominal bore 800mm x 200mm plain ended with flanged branch tee (for Air Valves) | nr | 32 |  | 0 | [10 empty] | 0 | 0 | 0 |  | 0
[16 empty] | 0 | 0 | 0 |  | 0
J323.2 | Nominal bore 800mm x 250mm plain ended with flanged branch level invert tee (for Washouts) | nr | 7 |  | 0 | [10 empty] | 0 | 0 | 0 |  | 0
All Flanged and or single end threading Tee
J324.40 | DN 800 x 100, PN 16 (for air valve) | nr | 5 |  | 0
0
J324.41 | DN 800 x 75, PN 16 (for air valve) | nr | 4 |  | 0
0
J324.42 | DN 800 x 50, PN 16 (for air valve) | nr | 23 |  | 0
0
| All Flanged Level Invert Tee |  |  |  | 0
0
J323.1 | DN 800 x 250, PN 16 (for washouts) | nr | 7 |  | 0
Blank Flanged Tee
J325 | DN 800 x 200, PN 16 (for future offtakes) | nr | 3 |  | 0
0
J34 | Ferrous Couplings |  |  |  | 0
0
| Straight Couplings |  |  |  | 0
0
J341.1 | DN 800, PN 16 | nr | 42 |  | 0
0
J35 | Ferrous Flange Adaptor |  |  |  | 0
0
J351.1 | DN 250, PN 16 | nr | 7 |  | 0
0
J352.1 | DN 800, PN 16 | nr | 15 |  | 0
0
0
PAGE TOTAL CARRIED TO COLECTION PAGE
J8 | Valves and Penstocks
J81 | All Flanged Gate Valve
Gate Valves for Washouts and line valves to be supplied complete with extension Spindle n.e. 2.0m and Tee- key. Air valve isolating valves to be supplied with wheel only. Contractor's rates to include for this
J811.1 | DN 50, PN16 | nr | 23 |  | 0
0
J811.2 | DN 80, PN16 | nr | 4 |  | 0
0
J811.3 | DN 100, PN16 | nr | 5 |  | 0
0
J811.4 | DN 250, PN 16, with Extension Spindle, length n.e. 3.0m without handwheel (for washouts) | nr | 7 |  | 0
0
J814.1 | DN 800, PN 16 with handwheel, gear mechanism and in-built bypass vavlve | nr | 2 |  | 0
0
J86 | Air Valve |  |  |  | 0
0
J861.1 | Flanged Air Valves shall be Anti shock combination air valves, full bore single chamber double function combination air valve with a built in anti-water hammer non slam surge prevention system. The air valve allows release of air pockets from pressurized pipelines, and admits large volume of air in the event of pipe draining/burst, to prevent vacuum and negative Pressure conditions |  |  |  | 0
0
J861.1.1 | DN 50, PN 16 | nr | 23 |  | 0
0
J861.1.2 | DN 80, PN 16 | nr | 4 |  | 0
0
J861.1.3 | DN 100, PN 16 | nr | 5 |  | 0
0
Water Meters
J381.7 | Supply and install a Nominal bore 800mm dia electromagnetic master meter with AMR capability, Lithium battery with a life of 5 yrs.as specified and approved by the Engineer. Rate to include all jointing/fittings materials and chamber installation as per drawings | nr | 2
PAGE TOTAL CARRIED TO COLECTION PAGE
CLASS K: PIPEWORK - MANHOLES AND PIPEWORK ANCILLARIES
Chambers, ducts, culverts, crossings, thrust, anchor blocks, reinstatement and others pipework ancillaries.
Note:- Items for Work in this class shall include:- - Excavation, preparation of surfaces, disposal of surplus excavated material, shoring sides of excavation, backfilling and removal of redundant services. - Concrete, Reinforcement, Formwork, Joints and Finishes.
K21 | IN SITU CONCRETE CHAMBERS
K211 | Provide all materials and construct reinforced concrete chambers, internal dimensions 1800mm x 1200mm. Include for supply and fixing of removable precast concrete covers, step irons, compacted granular fill, rendering of exposed blockwork etc. | nr | 46 |  | 0
K6 | Crossings
K61 | Allow for gulley crossings, including all couplings, reinforced concrete piers, surrounds, bearings etc. Length n.e 30m | nr | 2 |  | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
Micro-tunnelling below bituminous road
Rates quoted shall be deemed to include for costs incurred on traffic control, signage and safety measures during execution of the works.
K692 | Micro-tunnelling below the bituminous road. Nominal bores 800 mm | m | 30 |  | 0
K694 | Extra over microtunnelling in rock | m3 | 12 |  | 0
Reinstatement
Breaking up, temporary and permanent reinstatement of roads
K732.1 | Tarmac/paved roads. Pipe nominal bore 700 - 900mm | m | 20 |  | 0
K732.2 | Gravel Roads. Pipe nominal bore 700 - 900mm. | m | 200 |  | 0
Other Pipework Ancillaries
PAGE TOTAL CARRIED TO COLECTION PAGE
Supply and erect precast concrete marker post for the following:-
K820.1 | Pipeline marker post-inscribed 'WM ' | nr | 58.7 |  | 0
K820.2 | Air valve marker post-inscribed 'AV' | nr | 32 |  | 0
K820.3 | Washout marker post-inscribed 'WO' | nr | 7 |  | 0
CLASS L: PIPEWORK - SUPPORTS AND PROTECTION, ANCILLARIES TO LAYING AND EXCAVATION
| Excavation of rock as defined in Specifications | [12 empty] | 0 |  | 0 | 0 |  |  | 0
[14 empty] | 0 |  | 0 | 0 |  |  | 0
L111 | Extras to excavation and backfilling of pipe trenches; Excavation of rock | m3 | 14968.5 |  | 0 | [8 empty] | 0 | 0 | 0 | 0 | 0 |  | 0
L121 | Extras to excavation and backfilling in chambers; Excavation of rock | m3 | 110.4 |  | 0 | [8 empty] | 0 | 0 | 0 | 0 | 0 |  | 0
Concrete thrust blocks
Thrust blocks - Class 20/20 Mass Concrete, Volume 0.2 - 0.5m3
L713.2 | For DN 800 11.5o bend | nr | 15 |  | 0
L713.3 | For DN 800 22.5o bend | nr | 20 |  | 0
L713.4 | For DN 800 45o bend | nr | 12 |  | 0
Thrust blocks - RC, Class 25/20 Volume 0.5 - 1.5m3
L713.5 | For DN 800 90o bend | nr | 10 |  | 0
| Slip anchors on steep sections of the pipe profile as shown on drawings | [12 empty] | 0 | 0 |  | 0 | 0
[14 empty] | 0 | 0 |  | 0 | 0
L834.1 | Slip anchors, height 1.5 - 2.0m, pipe nominal bore 400mm | nr | 5 |  | 0 | [8 empty] | 0 | 0 |  | 0 | 0
PAGE TOTAL CARRIED TO COLECTION PAGE
X1.1 | Provide all materials and construct reinforced concrete SWAB CATCHER chambers, internal dimensions 4800mm x 3300mm. Include for supply and fixing of removable precast concrete covers, step irons, compacted granular fill, rendering of exposed blockwork etc. Supply and install all the accompanying fittings for the SWAB CATCHER chamber as per the drawings and according to the specifications. | nr | 2 |  | 0
X1.2 | Provide all materials and construct reinforced concrete SWAB LAUNCHER chambers, internal dimensions 4800mm x 3300mm. Include for supply and fixing of removable precast concrete covers, step irons, compacted granular fill, rendering of exposed blockwork etc. Supply and install all the accompanying fittings for the SWAB LAUNCHER chamber as per the drawings and according to the specifications. | nr | 2 |  | 0
0
X1.3 | Supply DN 400mm pressure sustaining valve and all the accompanying fittings, doubel flanged, stainless steel type 303 of volatge 240V/50Hz AC in accordance with the specifications and as approved by the engineer | nr | 4 |  | 0
PAGE TOTAL CARRIED TO COLECTION PAGE
BILL 2 Collection Page
1 | BROUGHT FORWARD FROM PAGE 1 |  |  |  | 0
2 | BROUGHT FORWARD FROM PAGE 2 |  |  |  | 0
3 | BROUGHT FORWARD FROM PAGE 3 |  |  |  | 0
4 | BROUGHT FORWARD FROM PAGE 4 |  |  |  | 0
5 | BROUGHT FORWARD FROM PAGE 5 |  |  |  | 0
6 | BROUGHT FORWARD FROM PAGE 6 |  |  |  | 0
7 | BROUGHT FORWARD FROM PAGE 7 |  |  |  | 0
BILL 2 COLLECTION CARRIED TO GRAND SUMMARY

## Bill No. 5 - Dayworks
BILL No. 5 - DAYWORKS
ITEM | DESCRIPTION | UNIT | QTY | RATE (KShs) | AMOUNT (KShs)
1.1 | LABOUR
The rates inserted hereafter should include all such costs as insurance, travel time, overtime expenses, accomodation, use and maintenance of small tools of trade, Contractors overheads and profit. Only time engaged upon work instructed by the Engineer under this Bill will be paid for.
1.1.1 | Unskilled labour | hr | 1600 |  | 0
1.1.2 | Foreman | hr | 180 |  | 0
1.1.3 | Driver | hr | 300 |  | 0
1.1.4 | Mason | hr | 300 |  | 0
1.1.5 | Carpenter | hr | 200 |  | 0
1.1.6 | Plumber | hr | 100 |  | 0
1.1.7 | Electrician | hr | 200 |  | 0
1.1.8 | Plant Operator | hr | 400 |  | 0
1.1.9 | Supervisor | hr | 200 |  | 0
1.1.10 | Pipelayer | hr | 400 |  | 0
1.1.11 | Painter | hr | 200 |  | 0
1.1.12 | Concretor | hr | 400 |  | 0
1.1.13 | Technician | hr | 200 |  | 0
1.1.14 | Watchman | hr | 600 |  | 0
PAGE TOTAL FOR LABOUR CARRIED TO SECTION COLLECTION SHEET |  |  |  |  | 0
BILL No. 5 - DAYWORKS
ITEM | DESCRIPTION | UNIT | QTY | RATE (KShs) | AMOUNT (KShs)
1.2 | MATERIALS
Materials shall comply with the relevant Technical Specifications and shall be subject to the approval of the Resident Engineer. The rate to include for delivery, storage, handling, Contractor's overheads, etc.
1.2.1 | Building sand | ton | 150 |  | 0
1.2.2 | Ordinary portland cement in 50 kg bags | No. | 500 |  | 0
1.2.3 | Fine aggregate | ton | 150 |  | 0
1.2.4 | Coarse aggregate | ton | 150 |  | 0
1.2.5 | 150mm Blockwork | m2 | 150 |  | 0
1.2.6 | 200mm Blockwork | m2 | 200 |  | 0
1.2.7 | Reinforcement fabric mesh. | m2 | 500 |  | 0
1.2.8 | Reinforcement steel. | ton | 25 |  | 0
1.2.9 | Concrete Class 25 | m3 | 50 |  | 0
1.2.10 | Imported Fill | m3 | 750 |  | 0
1.2.11 | Hardcore | m3 | 100 |  | 0
1.2.12 | Formwork | m2 | 500 |  | 0
1.2.13 | Petrol | L | 750 |  | 0
1.2.14 | Diesel | L | 500 |  | 0
1.2.15 | Lubricants | L | 200 |  | 0
1.2.16 | Epoxy Paint | L | 200 |  | 0
1.2.17 | Emulsion Paint | L | 200 |  | 0
1.2.18 | Gloss Paint | L | 100 |  | 0
1.2.19 | Wrought Finish Formwork | m2 | 200 |  | 0
1.2.20 | Smooth Finish Formwork | m2 | 250 |  | 0
PAGE TOTAL FOR MATERIAL CARRIED TO SECTION COLLECTION SHEET |  |  |  |  | 0
BILL No. 5 - DAYWORKS
ITEM | DESCRIPTION | UNIT | QTY | RATE (KShs) | AMOUNT (KShs)
1.3 | EQUIPMENT
Rates to include for all operation and maintenance of equipment, cost of fueling and lubrication, etc.
1.3.1 | Excavator | hr | 50 |  | 0
1.3.2 | Dozer 70Kw | hr | 200 |  | 0
1.3.3 | Grader Tractor | hr | 200 |  | 0
1.3.4 | Mobile generator 15 kVA | hr | 200 |  | 0
1.3.5 | 4 WD Pickup 1 tonne | hr | 250 |  | 0
1.3.6 | Concrete mixer type 5/3.5 | hr | 150 |  | 0
1.3.7 | Concrete dumper 0.5 cu.m. | hr | 150 |  | 0
1.3.8 | Concrete vibrator poker type N.D. 50 mm | hr | 150 |  | 0
1.3.9 | Dewatering pump 50mm dia suction end | hr | 300 |  | 0
1.3.10 | Air Compressor (5,000 l/min) | hr | 100 |  | 0
1.3.11 | Tipper Truck 7 tonne | hr | 150 |  | 0
1.3.12 | Tipper Truck 15 tonne | hr | 150 |  | 0
1.3.13 | Oxy-acetylene cutting and welding set including oxygen and acetylene gases. | hr | 150 |  | 0
1.3.14 | Electrical welding set including electrodes | hr | 150 |  | 0
PAGE TOTAL FOR EQUIPMENT CARRIED TO SECTION COLLECTION SHEET |  |  |  |  | 0
BILL No. 5 - DAYWORKS
ITEM | DESCRIPTION | UNIT | QTY | RATE (KShs) | AMOUNT (KShs)
SECTION COLLECTION PAGE
1 | BROUGHT FORWARD FROM PAGE 1 |  |  |  | 0
2 | BROUGHT FORWARD FROM PAGE 2 |  |  |  | 0
3 | BROUGHT FORWARD FROM PAGE 3 |  |  |  | 0
BILL 5 TOTAL CARRIED TO GRAND SUMMARY |  |  |  |  | 0

## Bill No. 3 - Reservoir
BILL No. 3 - 5,000 m3 Kakuyuni Reservoir
ITEM | DESCRIPTION | UNIT | QUANTITY | RATE | AMOUNT
No. |  |  |  | (Kshs) | (Kshs) | cts
1 | STORAGE RESERVOIR (5000m3)
1.1 | GENERAL
1.1.1 | Water Tightness Testing of the Tank in accordance with the Specifications to the satisfaction of the Engineer. Include for provision of water from approved source. | Item | L.S |  | 0
1.1.2 | Cleansing and Sterilisation of the 5,000m3 Tank in accordance with specifications. Rate to include for provision of water, all required chemicals and carrying out relevant tests as well as safe disposal of used water, all to Engineer's approval. | Item | L.S |  | 0
1.1.3 | Pressure Testing, Cleansing and Sterilisation of all Tank Pipework (Inlet, Outlet, Washout, Overflow) in accordance with Specifications. Rate to include for provision of water, all required chemicals and carrying out relevant tests as well as safe disposal of used water, all to Engineer's approval. | Item | L.S |  | 0
1.2 | EARTHWORKS
The rates shall include for all strutting, shuttering, stabilising the excavation faces, and keeping the excavation free of water by pumping, bailing or other means
Bulk excavations and top soil stripping for all structures at the Reservoir site are measured under Section 2 of this bill (Site & Ancillary Works)
Excavate below stripped level to formation level in common material, part backfill after construction and remainder, cart away to tips identified by the Contractor in liaison with Local Authorities or use as fill on site, all as directed by the Engineer.
1.2.1 | Maximum depth n.e. 1.0 m | m3 | 1700 |  | 0
0
1.2.2 | -Ditto- but maximum depth 1.0 m to 2.0 m | m3 | 1700 |  | 0
0
1.2.3 | -Ditto- but maximum depth 2.0 m to 5.0 m | m3 | 5300 |  | 0
0
1.2.4 | -Ditto- but maximum depth exceeding 5.0 m | m3 | 4700 |  | 0
0
1.2.5 | Provide and place approved hardcore packing, hand packed and compacted to Egineer's approval, maximum 300mm thick layer. Rate to include for provision, packing and compaction. | m3 | 550 |  | 0
PAGE TOTAL CARRIED TO COLLECTION PAGE |  |  |  |  | 0
1.2.6 | Extra Over excavation items for excavation in rock Class 'A', blasting not permitted (Provisional) | m3 | 540 |  | 0
0
1.2.7 | -Ditto- but in rock Class 'B' | m3 | 800 |  | 0
0
1.2.8 | -Ditto- but in rock Class 'C' | m3 | 1340 |  | 0
1.3 | CONCRETE WORKS
Provide, Mix and Place Concrete as Directed
1.3.1 | Plain concrete Class 15/20 in 75mm thick blinding layer under base slab of tank | m2 | 1550 |  | 0
0
| Structural Concrete Class 25/20mm Maximum Aggregate as Described in:- |  |  |  | 0
0
1.3.2 | Base - external walls base including key and splay | m3 | 330 |  | 0
0
1.3.3 | Base - Internal Partition wall | m3 | 55 |  | 0
0
1.3.4 | Base slab -including sloping faces | m3 | 182 |  | 0
0
1.3.5 | Bases to columns | m3 | 18 |  | 0
0
1.3.6 | Bases to internal baffle walls | m3 | 14 |  | 0
0
1.3.7 | Base to overflow chamber | m3 | 1 |  | 0
0
1.3.8 | Roof slab including all upstands | m3 | 336 |  | 0
0
1.3.9 | External walls (thickness 500 mm) | m3 | 180 |  | 0
0
1.3.1 | External walls (thickness 300 mm) | m3 | 115 |  | 0
0
1.3.11 | Partition wall (thickness 300mm) | m3 | 55 |  | 0
0
1.3.12 | Baffle walls | m3 | 100 |  | 0
0
1.3.13 | Walls - washout sump | m3 | 1 |  | 0
0
1.3.14 | Walls - overflow chamber | m3 | 1 |  | 0
0
1.3.15 | Colums (excluding top flared heads) | m3 | 12 |  | 0
0
1.3.16 | Column Heads | m3 | 6 |  | 0
0
PAGE TOTAL CARRIED TO COLLECTION PAGE |  |  |  |  | 0
1.4 | REINFORCEMENT |  |  |  | 0
0
| Provide and Fix High Tensile Steel Reinforcement to SRN 127 including Ctting, Bending, Propping with Spacers and Tying as specified :- |  |  |  | 0
0
1.4.1 | Reinforcement Bars, all diameters | Kg | 210900 |  | 0
0
1.4.2 | Steel fabric to BS 4483: A252 squaremesh, nominal mass 3-4kg/m2. | m2 | 910 |  | 0
0
1.5 | FORMWORK |  |  |  | 0
0
| Provide and Fix Shuttering Including Propping, Strutting and Striking, all as specified. Rate to include for formation of chamfers at concrete edges where specified. |  |  |  | 0
0
| (i) Vertical Formwork - Class F1 Finish |  |  |  | 0
0
1.5.1 | External sides of 200 mm base slab of tank | m | 170 |  | 0
1.5.2 | Sides of key; width 0.4 m to 1.0 m | m2 | 305 |  | 0
1.5.3 | External sides of washout sump, width 1.0 m | m2 | 6 |  | 0
0
| (ii) Vertical Formwork - Class F3 Finish |  |  |  | 0
0
1.5.4 | Internal sides of washout sumps, width 0.4 m to 1.0 m | m2 | 4 |  | 0
0
1.5.5 | Inner sides of access and inspection manholes, width 0.4 m to 2.0 m | m2 | 18 |  | 0
0
1.5.6 | Sides of partition wall base slab, width n.e. 0.5m | m2 | 35 |  | 0
0
1.5.7 | Sides of overflow chamber, width 1.0 m to 1.5 m | m2 | 11 |  | 0
0
1.5.8 | Outer sides of access and inspection manholes upstands, 300 mm high; width 1.0 m to 2.0 m | m2 | 22 |  | 0
0
1.5.9 | Inner sides of roof upstands 300 mm high, width exceeding 2 m | m2 | 50 |  | 0
0
1.5.10 | Outer sides of roof upstands 550 mm high width exceeding 2 m | m2 | 95 |  | 0
0
1.5.11 | Outer sides of external walls, width exceeding 2 m | m2 | 800 |  | 0
0
1.5.12 | Inner sides of external walls, wall thickness 0.3m to 0.5m, width exceeding 2.0 m | m2 | 800 |  | 0
0
1.5.13 | Sides of partition wall, width exceeding 2.0m | m2 | 340 |  | 0
0
1.5.14 | Baffle walls, width exceeding 2.0 m | m2 | 1010 |  | 0
0
1.5.15 | Sides of columns; width 0.3 m | m | 150 |  | 0
0
1.5.16 | Sides of columns; width 0.1 m | m | 100 |  | 0
0
PAGE TOTAL CARRIED TO COLLECTION PAGE |  |  |  |  | 0
1.5.17 | Sides of column bases; width 0.3 m | m | 150 |  | 0
0
1.5.18 | Sides of baffle walls bases; width 0.3 m | m | 200 |  | 0
0
| (iii) Horizontal Formwork - Class F3 Finish |  |  |  | 0
0
1.5.19 | Soffits of overflow channel | m2 | 4 |  | 0
0
1.5.20 | Soffit of roof slab, width exceeding 2.0 m | m2 | 1400 |  | 0
0
| (iv) Sloping Formwork - Class F3 Finish |  |  |  | 0
0
1.5.21 | Splay on wall at overflow chamber, width 0.1 m to 0.3 m | m | 2 |  | 0
0
1.5.22 | Splay on base slab, width 0.1 m 0.3 m | m | 300 |  | 0
0
1.5.23 | Splay in wall, width 0.1 m to 0.3 m | m | 150 |  | 0
0
1.5.24 | Splay at column heads, width 0.4 m to 1.0 m | m2 | 40 |  | 0
0
1.5.25 | Allow for 75 mm x 75 mm rebate in walls of overflow chamber for precast concrete slabs | m | 5 |  | 0
0
1.5.26 | - Ditto - but 50 mm x 50 mm rebates for manhole covers | m | 30 |  | 0
1.5.27 | Allow for fillet to form 25 mm x 25 mm chamfer for all exposed concrete edges | m | 550 |  | 0
1.5.28 | Allow for 12 mm dia. half round fillet for drip mould round soffit of roof slab overhang | m | 155 |  | 0
0
1.5.29 | Boxing out for 800 mm diameter inlet pipe in 300mm thick concrete wall of tank and making good after installation of pipework | Nr | 2 |  | 0
0
1.5.30 | Boxing out for 500 mm diameter outlet pipe in 200mm thick concrete base slab of tank and making good after installation of pipework | Nr | 2 |  | 0
0
5.31 | Boxing out for 300 mm diameter suction pipe in 200mm thick concrete base slab of tank and making good after installation of pipework | Nr | 2 |  | 0
0
1.5.31 | Boxing out for 500 mm diameter overflow pipe in 200mm thick concrete base of overflow chamber and making good after installation of pipework | Nr | 2 |  | 0
0
1.5.32 | - Ditto - but for 250mm diameter scour pipe in 200mm thick concrete wall of scour sump | Nr | 2 |  | 0
0
1.5.33 | - Ditto - but for 250mm diameter scour pipe in 500mm thick concrete walls | Nr | 2 |  | 0
0
PAGE TOTAL CARRIED TO COLLECTION PAGE |  |  |  |  | 0
1.6 | CONCRETE SURFACE FINISH |  |  |  | 0
0
1.6.1 | Provide Class UF3 Finish for top of base slab of tank | m2 | 1320 |  | 0
0
1.7 | CONSTRUCTION JOINTS - WATER BARS |  |  |  | 0
0
| Provide and install the following waterstops in construction joints including all surface treatment, formwork, forming of rebate and sealing of rebate with polysulphide sealant, all as per drawings and specification |  |  |  | 0
0
1.7.1 | Open surface with filler, average width n.e. 0.5 m | m2 | 200 |  | 0
0
1.7.2 | Formed surface with filler, average width n.e. 0.5 m | m2 | 120 |  | 0
0
1.7.3 | uPVC horizontal waterstops, rear guard type, width 200 mm | m | 150 |  | 0
0
1.7.4 | uPVC vertical waterstops, width 200 mm | m | 450 |  | 0
0
1.7.5 | Sealed 20 mm x 20 mm rebates with polysulphide joint sealant | m | 600 |  | 0
0
1.8 | PIPEWORK - FITTINGS & VALVES |  |  |  | 0
0
| Supply, Transport to Site and Store in Secure Place, Including all Jointing Material, Bolts, Gaskets, Packing, Jointing Glues, etc. as Applicable |  |  |  | 0
0
| (i) Inlet Pipework - Epoxy Lined Ferrous Pipes and Fittings |  |  |  | 0
0
1.8.1 | 800mm dia. Coupling | Nr | 3 |  | 0
0
1.8.2 | 800mm dia. Flanged spigot pipe, 1200mm long | Nr | 2 |  | 0
0
1.8.3 | 800mm dia. All flanged 45o bend | Nr | 1 |  | 0
0
1.8.4 | 800mm dia. Plain ended pipe, 30000mm long With Couplings (cut to suit on site) | Nr | 1 |  | 0
1.8.5 | 800mm dia. Plain ended pipe, 1200mm long with puddle flange at 650mm from one end | Nr | 1 |  | 0
1.8.6 | 800mm x 600mm dia. All flanged tee | Nr | 1 |  | 0
0
1.8.7 | 600mm dia. All flanged gate valve with an extended spindle 1800mm long, head stock and hand wheel | Nr | 2 |  | 0
0
1.8.8 | 600mm dia. Flange adaptor | Nr | 3 |  | 0
0
1.8.9 | 600mm dia. Flanged spigot pipe, 1835mm long with puddle flange at 625mm from plain end | Nr | 1 |  | 0
0
1.8.10 | 600mm dia. All flanged 90o short radius bend | Nr | 4 |  | 0
0
1.8.11 | 600mm dia. All flanged pipe, 1300mm long with a puddle flange at 450mmm from one end | Nr | 2 |  | 0
PAGE TOTAL CARRIED TO COLLECTION PAGE |  |  |  |  | 0
0
1.8.12 | 600mm dia. Flanged ball float valve (series 1042-Biwater or approved equivalent) | Nr | 2 |  | 0
0
1.8.13 | 600mm dia. Flanged spigot pipe, 1000mm long | Nr | 2 |  | 0
0
1.8.14 | 800mm x 600mm dia. All flanged concentric taper | Nr | 1 |  | 0
0
1.8.15 | 600mm dia. Plain ended pipe, 1200mm long with puddle flange at 625mm from one end | Nr | 1 |  | 0
0
1.8.16 | 600mm dia. Coupling | Nr | 3 |  | 0
0
1.8.17 | 600mm dia. Plain ended pipe, 12000mm long | Nr | 2 |  | 0
0
1.8.18 | 600mm dia. Flanged Spigot pipe, 10000mm long (cut to suit on site) | Nr | 1 |  | 0
0
1.8.19 | 600mm dia. All flanged 90o bend | Nr | 1 |  | 0
0
1.8.20 | 600mm dia. Flanged spigot pipe, 2000mm long (cut to suit on site) | Nr | 1 |  | 0
0
| (ii) Outlet Pipework- Epoxy Lined Ferrous Pipes and Fittings |  |  |  | 0
0
1.8.21 | 500mm dia. Special flanged bellmouth, length 800mm with puddle flange at 600mm from flanged end | Nr | 2 |  | 0
0
1.8.22 | 500mm dia. all flanged 90o bend | Nr | 3 |  | 0
0
1.8.23 | 500mm dia. flanged spigot pipe, length 6500mm long (cut to suit on site | Nr | 2 |  | 0
0
1.8.24 | 500mm dia. Coupling | Nr | 7 |  | 0
0
1.8.25 | 500mm dia. plain ended pipe, 1200mm long with puddle flange at 725mm from one end | Nr | 1 |  | 0
0
1.8.26 | 500mm dia. Flange Adaptor | Nr | 3 |  | 0
0
1.8.27 | 500mm dia. double flanged gate valve with extended spindle 2200mm long, headstock and handwheel | Nr | 2 |  | 0
1.8.28 | 500mm x 500mm dia. All flanged tee | Nr | 1 |  | 0
1.8.29 | 500mm dia. Flanged spigot pipe, 1300mm long (cut to suit on site) | Nr | 1 |  | 0
1.8.3 | 500mm dia. Flanged spigot pipe, 1200mm long | Nr | 1 |  | 0
0
1.8.31 | 500mm dia. Plain ended pipe, 12000mm long (cut to suit on site) | Nr | 1 |  | 0
0
1.8.32 | 500mm dia. Plain ended pipe, 1200mm long with puddle flange at 500mm from one end | Nr | 1 |  | 0
PAGE TOTAL CARRIED TO COLLECTION PAGE |  |  |  |  | 0
1.8.33 | 500mm dia. Flanged spigot pipe, 1200mm long with puddle flange at 500mm from the plain end | Nr | 1 |  | 0
0
1.8.34 | 500mm dia. Plain ended pipe, 7000mm long (cut to suit on site) | Nr | 1 |  | 0
0
1.8.35 | 500mm dia. Plain ended pipe, 1200mm long with puddle flange at 450mm from one end (Mark 15) | Nr | 1 |  | 0
0
1.8.36 | 500mm dia. Electromagnetic Water Meter, complete with all requisite accesories (Mark 16) | Nr | 1 |  | 0
0
1.8.37 | 500mm dia. Flanged Spigot pipe, 1200mm long with puddle flange at 450mm from one end | Nr | 1 |  | 0
0
| (iii) Scour Pipework - Epoxy Lined Ferrous Pipes and Fittings |  |  |  | 0
0
1.8.38 | 250mm dia. Plain ended pipe, 5200mm long with puddle flange at 100mm from one end (cut to suit on site) | Nr | 2 |  | 0
0
1.8.39 | 250mm dia. Coupling | Nr | 2 |  | 0
0
1.8.40 | 250mm dia. Flanged Spigot pipe, 1200mm long with puddle flange at 655mm from one end | Nr | 2 |  | 0
0
1.8.41 | 250mm dia.all flanged gate valve with an extended spindle 2000mm, head stock and hand wheel | Nr | 2 |  | 0
0
1.8.42 | 250mm dia. Single flanged 90o bend | Nr | 2 |  | 0
0
| (iv) Overflow Pipework - Epoxy Lined Ferrous Pipes and Fittings |  |  |  | 0
0
1.8.43 | 500mm dia. Flanged spigot pipe, 1500mm long with puddle flange at 100mm from spigot end | Nr | 2 |  | 0
0
1.8.44 | 500mm dia. All flanged 45o bend | Nr | 2 |  | 0
0
1.8.45 | 500mm dia. Flanged spigot pipe,2250mm long with spigot end bevelled | Nr | 2 |  | 0
(i) Inlet Pipework - Epoxy Lined Ferrous Pipes and Fittings
1.8.46 | 800mm dia. Coupling | Nr | 3 |  | 0
0
1.8.47 | 800mm dia. Flanged spigot pipe, 1200mm long | Nr | 2 |  | 0
0
1.8.48 | 800mm dia. All flanged 45o bend | Nr | 1 |  | 0
0
1.8.49 | 800mm dia. Plain ended pipe, 30,000mm long With Couplings (cut to suit on sitea) | Nr | 1 |  | 0
0
PAGE TOTAL CARRIED TO COLLECTION PAGE |  |  |  |  | 0
1.8.50 | 800mm dia. Plain ended pipe, 1200mm long with puddle flange at 650mm from one end | Nr | 1 |  | 0
0
1.8.51 | 800mm x 600mm dia. All flanged tee | Nr | 1 |  | 0
0
1.8.52 | 600mm dia. All flanged gate valve with an extended spindle 1800mm long, head stock and hand wheel | Nr | 2 |  | 0
0
1.8.53 | 600mm dia. Flange adaptor | Nr | 3 |  | 0
0
1.8.54 | 600mm dia. Flanged spigot pipe, 1835mm long with puddle flange at 625mm from plain end | Nr | 1 |  | 0
0
1.8.55 | 600mm dia. all flanged 90o short radius bend | Nr | 4 |  | 0
0
1.8.56 | 600mm dia. All flanged pipe, 1300mm long with puddle flange at 450mmm from one end | Nr | 2 |  | 0
0
1.8.57 | 600mm dia. Flanged ball float valve (series 1042-Biwater or approved equivalent) | Nr | 2 |  | 0
0
1.8.58 | 600mm dia. Flanged spigot pipe, 1000mm long | Nr | 2 |  | 0
0
1.8.59 | 800mm x 600mm dia. All flanged concentric taper | Nr | 1 |  | 0
0
1.8.60 | 600mm dia. Plain ended pipe, 1200mm long with puddle flange at 625mm from one end | Nr | 1 |  | 0
0
1.8.61 | 600mm dia. Coupling | Nr | 3 |  | 0
0
1.8.62 | 600mm dia. Plain ended pipe, 12000mm long | Nr | 2 |  | 0
0
1.8.63 | 600mm dia. Flanged Spigot pipe, 10000mm long (cut to suit on site) | Nr | 1 |  | 0
0
1.8.64 | 600mm dia. All flanged 90o bend | Nr | 1 |  | 0
0
1.8.65 | 600mm dia. Flanged spigot pipe, 2000mm long (cut to suit on site) | Nr | 1 |  | 0
(ii) Outlet Pipework- Epoxy Lined Ferrous Pipes and Fittings
1.8.66 | 500mm dia. Special flanged bellmouth, length 800mm with puddle flange at 600mm from flanged end | Nr | 2 |  | 0
0
1.8.67 | 500mm dia. all flanged 90o bend | Nr | 3 |  | 0
0
1.8.68 | 500mm dia. flanged spigot pipe, length 6500mm long (cut to suit on site | Nr | 2 |  | 0
0
1.8.69 | 500mm dia. Coupling | Nr | 7 |  | 0
0
1.8.70 | 500mm dia. plain ended pipe, 1200mm long with puddle flange at 725mm from one end | Nr | 1 |  | 0
0
1.8.71 | 500mm dia. Flange Adaptor | Nr | 3 |  | 0
PAGE TOTAL CARRIED TO COLLECTION PAGE |  |  |  |  | 0
0
1.8.72 | 500mm dia. double flanged gate valve with extended spindle 2200mm long, headstock and handwheel | Nr | 2 |  | 0
0
1.8.73 | 500mm x 500mm dia. All flanged tee | Nr | 1 |  | 0
0
1.8.74 | 500mm dia. Flanged spigot pipe, 1300mm long (cut to suit on site) | Nr | 1 |  | 0
1.8.75 | 500mm dia. Flanged spigot pipe, 1200mm long | Nr | 1 |  | 0
0
1.8.76 | 500mm dia. Plain ended pipe, 12000mm long (cut to suit on site) | Nr | 1 |  | 0
0
1.8.77 | 500mm dia. Plain ended pipe, 1200mm long with puddle flange at 500mm from one end | Nr | 1 |  | 0
0
1.8.78 | 500mm dia. flanged spigot pipe, 1200mm long with puddle flange at 500mm from the plain end | Nr | 1 |  | 0
0
1.8.79 | 500mm dia. Plain ended pipe, 7000mm long (cut to suit on site) | Nr | 1 |  | 0
0
1.8.80 | 500mm dia. Plain ended pipe, 1200mm long with puddle flange at 450mm from one end | Nr | 1 |  | 0
0
1.8.81 | 500mm dia. Electromagnetic Water Meter complete with all requisite accessories | Nr | 1 |  | 0
0
1.8.82 | 500mm dia. Flanged Spigot pipe, 1200mm long with puddle flange at 450mm from one end | Nr | 1 |  | 0
0
| (iii) Scour Pipework - Approved Lined Ferrous Pipes and Fittings |  |  |  | 0
0
1.8.83 | 250mm dia. Plain ended pipe, 5200mm long with a puddle flange 100mm from one end (cut to suit on site) | Nr | 2 |  | 0
0
1.8.84 | 250mm dia. Coupling | Nr | 2 |  | 0
0
1.8.85 | 250mm dia. Flanged Spigot pipe, 1200mm long with a puddle flange 655mm from one end | Nr | 2 |  | 0
0
1.8.86 | 250mm dia.all flanged gate valve with an extended spindle 2000mm, head stock and hand wheel | Nr | 2 |  | 0
1.8.87 | 250mm dia. Single flanged 90o bend | Nr | 2
(iv) Overflow Pipework - Expoxy Lined Ferrous Pipes and Fittings
1.8.88 | 500mm dia. Flanged spigot pipe, 1500mm long with puddle flange at 100mm from spigot end | Nr | 2 |  | 0
0
1.8.89 | 500mm dia. All flanged 45o bend | Nr | 2 |  | 0
0
1.8.90 | 500mm dia. Flanged spigot pipe,2250mm long with spigot end bevelled | Nr | 2 |  | 0
PAGE TOTAL CARRIED TO COLLECTION PAGE |  |  |  |  | 0
0
1.9 | METALWORK |  |  |  | 0
0
| Rate to include for, but not limited to all fabrication, welding, jointing, galvanizing, painting works, transportation to site and installation; including rawl bolts, hinges, locking mechanisms, etc. where applicable. All to Engineer's approval. |  |  |  | 0
0
| All steelwork to be completely cleaned by acid dipping prior to galvanising |  |  |  | 0
0
| Supply and Install: |  |  |  | 0
0
1.9.1 | Galvanised mild steel ladders, height n.e. 6000 mm installed internally in the Tank, as per details on | Nr | 4 |  | 0
0
1.9.2 | -Ditto- but for Galvanized Mild Steel ladders, height n.e 6000mm installed externally to the tank | Nr | 2 |  | 0
0
1.9.3 | Lockable mild steel chequred plate covers over access manholes to tank as per details , for manhole size 1020mmx1020mm | Nr | 4 |  | 0
0
1.9.4 | Ditto - but over inspection manholes to tank for manhole size 2000mmx1600mm | Nr | 2 |  | 0
0
1.1 | MISCELLANEOUS WORK |  |  |  | 0
0
| Provide and Place |  |  |  | 0
0
1.10.1 | 3 layers of 4mm thick, 300mm wide, joint filling material at wall to roof slab interface - Polyflex APP modified Membrane as supplied by Kenbro Industries or approved equivalent - including all surface preparation, etc., to the manufacturer's detailed instructions. | m | 150 |  | 0
0
1.10.2 | Gauge 1000 polythene sheeting on blinding below base slab | m2 | 1550 |  | 0
0
1.10.3 | 150 mm thick layer of pumice on roof slab of tank | m2 | 1290 |  | 0
0
1.10.4 | Supply and install vent pipes on roof of tank as per details . Rate to include for painting with 3 coats of approved epoxy paint on one coat of aproved primer. | Nr | 24 |  | 0
PAGE TOTAL CARRIED TO COLLECTION PAGE |  |  |  |  | 0
2 | SITE AND ANCILLARY WORKS AT STORAGE RESERVOIR
2.1 | DEMOLITION, SITE CLEARANCE AND GENERAL EXCAVATION
2.1.1 | Clear area within the Storage Reservoir site of all grass, bushes, shrubs, hedges, grub up roots and cart away to approved tips identified by the Contractor in liaison with Local Authorities, all as directed by the Engineer | m2 | 6050 |  | 0
0
2.1.2 | Cut down trees, grub up roots and cart away to approved tips identified by the Contractor in liaison with Local Authorities, all as directed by the Engineer. Girth n.e. 1.2m | Nr | 12 |  | 0
0
2.1.3 | -Ditto- but girth 1.2 - 2.4m | Nr | 5 |  | 0
0
2.1.4 | Demolish existing concrete plinths and walls in buildings and structures and cart away surplus to approved tips identified by the Contractor in liaison with the Local Authorities, as directed by the Engineer | m3 | 6 |  | 0
0
| Top Soil Stripping |  |  |  | 0
0
2.1.5 | Excavate over site for structures, roads, etc. average 150mm deep to remove vegetable soil and stack part of material for use as and where directed by the Engineer, cart away surplus to tips identified by the Contractor in liaision with the Local Authorities | m2 | 4000 |  | 0
0
| Earthworks and Grading |  |  |  | 0
0
2.1.6 | Excavate approximately 300mm below stripped surface to formation level of roads, footpaths and verges including compaction of areas, stack approved material for reuse as fill and cart away surplus to approved tips identified by he Contractor in liaison with the Local Authorities, all as directed by the Engineer | m3 | 120 |  | 0
0
2.1.7 | Fill using approved suitable excavated material stacked on site, compact in 150mm layers as specified under roads and verges compacted to suitable density as per Clause 304 of the Specifications. Compaction tests to be carried out and rates to inlcude for it. | m3 | 60 |  | 0
0
2.1.8 | -Ditto- around the Tank, including cutting and trimming of slopes | m3 | 50 |  | 0
0
2.1.9 | Fill using approved imported material, compact in 150mm layers as specified. Compact to suitable density as per Clause 304 of the Specifications. Compaction tests to be carried out and rates to inlcude for it. Contractor to identify suitable borrow pits as source of material. | m3 | 60 |  | 0
0
PAGE TOTAL CARRIED TO COLLECTION PAGE |  |  |  |  | 0
2.1.10 | Extra over Excavation items for excavation in rock Class 'A' - blasting not permitted (provisional) | m3 | 5 |  | 0
0
2.1.11 | Extra over Excavation items for excavation in rock Class 'B' - blasting not permitted (provisional) | m3 | 8 |  | 0
2.1.12 | Extra over Excavation items for excavation in rock Class 'C' - blasting not permitted (provisional) | m3 | 12 |  | 0
2.1.13 | Spread top soil stacked on site for reuse (Item 2.1.5) level and prepare for grassing and landscaping. Plant approved grass and maintain until it takes roots | m2 | 3000 |  | 0
0
2.2 | ROADS AND FOOTPATHS |  |  |  | 0
0
| Kerbs and Channels |  |  |  | 0
0
2.2.1 | Provide, lay and joint 255 mm x 125 mm precast concrete kerbs on and including 250 mm x 100 mm Class 15/20 concrete foundation and haunch 125 mm thick including all excavation, shuttering, jointing and bedding as specified | m | 75 |  | 0
0
2.2.2 | E.O. Item 2.2.1 for kerbs laid to radius n.e. 20 m | m | 8 |  | 0
0
2.2.3 | Provide, lay and joint 125 mm x 100 mm precast concrete channels on and including 225 mm x 125 mm Class 15/40 concrete bed and haunch 100 mm thick including all excavation, shuttering, jointing and bedding as specified | m | 75 |  | 0
0
2.2.4 | E.O. Item for channels laid to radius n.e. 3.0m | m | 8 |  | 0
0
2.2.5 | -Ditto - but for channels laid to radius n.e. 6.0m | m | 8 |  | 0
0
| Concrete Block Paved Roads |  |  |  | 0
0
| Sub-Base and Base Courses: Provide, Lay and Compact to required relative density as per Clause 304 of Specifications: |  |  |  | 0
0
2.2.6 | Hand packed hardcore compacted to CBR not less than 30 up to formation level (where road is in fill) | m3 | 100 |  | 0
0
2.2.7 | Base 200mm thick crusher run or quarry chips (hand packed), including for watering and stone dust blinding as directed. | m2 | 300 |  | 0
0
2.2.8 | 200mm murram, include for watering and stone dust blinding as directed | m2 | 300 |  | 0
0
2.2.9 | Provide and apply approved weed killer / herbicide to road surface in accordance with manufacturer's instructions | m2 | 300 |  | 0
0
| Concrete Block Paving (as Manufactured by Bamburi Special Products Ltd. or Other Approved Supplier) |  |  |  | 0
0
2.2.10 | Supply and lay Medium Duty Paving Blocks, 60mm thick, Minimum strength 37-41N/mm2 laid on and including 50mm thick sand bed and compacted by surface vibration | m2 | 300 |  | 0
PAGE TOTAL CARRIED TO COLLECTION PAGE |  |  |  |  | 0
| Footpaths |  |  |  | 0
0
| Provide and lay: |  |  |  | 0
0
2.2.11 | 100mm murram sub-base, compacted to Engineer's approval | m2 | 150 |  | 0
0
2.2.12 | 50mm thick concrete bed for footpath (Class 15) | m2 | 150 |  | 0
0
2.2.13 | Precast concrete paving in 600mm x 600mm x 50mm slabs jointed and grouted up in lime and sand (1:3) | m2 | 150 |  | 0
2.3 | FENCING AND GATES
2.3.1 | Excavate for post holes, provide all materials and construct chain link fence on concrete posts at 3m centre to centre as specified including straining posts at every 10th post and additional posts at corners. | m | 100 |  | 0
0
2.3.2 | Provide all materials and construct Pedestrian gate 2.0m wide including 2 Nr. Pillars, footings, | Nr | 1 |  | 0
0
3.3 | -Ditto - but 1.0m wide pedestrian gate | Nr | 1 |  | 0
0
2.4 | SURFACE WATER DRAINAGE |  |  |  | 0
0
| Precast Concrete Drains |  |  |  | 0
0
2.4.1 | Excavate trench for precast concrete invert block drain Type 'A' , including trimming of sides to receive courses and cart excavated material to tips. Depth to invert n.e. 1.0m. | m | 75 |  | 0
0
2.4.2 | -Ditto - but depth exceeding 1.0m | m | 175 |  | 0
0
2.4.3 | Provide, lay and joint precast concrete invert block drain Type 'A' on 100mm murram bed, including 75mm murram filling both sides for height of block | m | 250 |  | 0
0
2.4.4 | E.O. item 2.4.3 above for provisions, laying and jointing two courses (one each side) of precast concrete side slabs to Type 'A' drain on 75mm thick compacted murram bed | m | 75 |  | 0
0
2.4.5 | -Ditto - but with 4 courses (two on each side) | m | 75 |  | 0
0
2.4.6 | -Ditto - but with 6 courses (three on each side) | m | 100 |  | 0
0
2.4.7 | Provide, lay and joint to any radius, precast concrete invert block drain on 100mm murram bed including 75mm murram filling both sides for height of block. Price to include for all cutting, waste, etc. | m | 20 |  | 0
0
2.4.8 | E.O. item 2.4.7 above for provision, laying and jointing two courses (one each side) of precast concrete side slabs to invert block drain on 75mm block compacted murram bed. Price to include for all cutting, waste, etc. | m | 10 |  | 0
0
2.4.9 | -Ditto - but with 4 courses (two on each side) | m | 5 |  | 0
0
2.4.10 | -Ditto - but with 6 courses (three on each side) | m | 5 |  | 0
0
PAGE TOTAL CARRIED TO COLLECTION PAGE |  |  |  |  | 0
0
| Culvert Pipes and Storm Water Sewers (Provisional) |  |  |  | 0
0
2.4.11 | Excavate trench depth n.e. 2.5 m, supply, lay and joint 600mm diameter precast concrete ogee pipes including concrete haunch and surround, backfill after laying of pipes, compact and cart away surplus material to tips | m | 15 |  | 0
0
| Headwalls |  |  |  | 0
0
2.4.12 | Excavate for, provide all materials and construct 200 mm thick masonry headwalls including concrete Class 20/20 footings. | Nr | 2 |  | 0
2.5 | SCOUR / OVERFLOW DRAINAGE PIPELINE
2.5.1 | Excavate trench for 525mm dia. concrete S&S pipe for Scour/ Overflow drainage pipework, backfill after laying of pipes and cart away surplus to tips identified by the Contractor in liaison with Local Authorities as directed. Average depth n.e. 3.0m (Provisional) | m | 500 |  | 0
0
2.5.2 | Supply, lay, joint and test 525mm dia. concrete S&S pipes including Type 'BO' bed and surround.(Provisional length) | m | 500 |  | 0
0
| Manholes (Provisional) |  |  |  | 0
0
2.5.3 | Excavate for, provide all materials and install Reinforced Precast Concrete Circular Drainage Manholes, 1.2m diameter; on R.C. base slab, complete with benching, step irons, etc. Include for pipe installation, forming benching, Grade 'B' medium duty Cast Iron Covers, etc. Depth to invert n.e. 3.0m | Nr | 4 |  | 0
0
2.6 | VALVE CHAMBERS |  |  |  | 0
0
2.6.1 | Provide all materials, excavate for and construct Reinforced Concrete Inlet Valve Chamber, size 3300mm x 2600mm x 2250mm deep complete with precast concrete cover slab and step irons | Nr | 1 |  | 0
0
2.6.2 | -Ditto - but Reinforced Concrete Outlet Valve Chamber size 2400mm x 2500mm x 2750mm deep with GMS Cat ladder | Nr | 1 |  | 0
0
2.6.3 | -Ditto - but reinforced concrete scour/overflow chamber size 2200mm x 2200mm x 2800mm deep with GMS Cat ladder | Nr | 2 |  | 0
0
2.7 | MISCELLANEOUS |  |  |  | 0
0
2.7.1 | Provide all material, fabricate and install signboard for Storage Reservoir, dimensions 1150mm x 1200mm. Include for painting, decorating and anchoring of the signboard to the ground using 300mm x 300mm x 600mm deep mass concrete footing. Note: Final wording on signboard to be decided in consultation with the Employer. | Nr | 1 |  | 0
2.7.2 | Allow a Provisional Sum of Kshs. 500,000 to be used as directed by the Engineer for any other Works as may be deemed necessary on site. | Item | P.S
PAGE TOTAL CARRIED TO COLLECTION PAGE |  |  |  |  | 0
2.8 | COMPACTION TESTS AND COMPACTION OF TANK FORMATION SURFACE
2.8.1 | Allow for carrying out onsite compaction tests at formation levels of Tank structure using the Sand Displacement Method or other approved in-situ method. Rate to include for provision of all apparatus and materials and carrying out the test as per standard procedures. Tests to be carried out on at least 2Nr. locations on the Reservoir base to be selected by the Engineer. | Item | L.S |  | 0
2.8.2 | Allow for compaction of formation surface of the Tank if deemed necessary upon compaction tests. Rate to include for provision of adequate vibrating compaction equipment and compaction of formation level to relative density of 98% MDD; all as per Clause 304 of the Specifications. | m2 | 1550 |  | 0
PAGE TOTAL CARRIED TO COLLECTION PAGE |  |  |  |  | 0
Amount
(Kshs.)
| Page 1 of 15 |  |  |  | 0
| Page 2 of 15 |  |  |  | 0
| Page 3 of 15 |  |  |  | 0
| Page 4 of 15 |  |  |  | 0
| Page 5 of 15 |  |  |  | 0
| Page 6 of 15 |  |  |  | 0
| Page 7 of 15 |  |  |  | 0
| Page 8 of 15 |  |  |  | 0
| Page 9 of 15 |  |  |  | 0
| Page 10 of 15 |  |  |  | 0
Page 11 of 15
Page 12 of 15
Page 13 of 15
Page 14 of 15
Page 15 of 15
| Bill Total Carried to the Bill 3 of the Grand Summary |  | 0 |  | 0

## Bill No. 4 - Pump Station
BILL 4 - PUMP STATION
ITEM NO. | DESCRIPTION | UNIT | QTY | RATE (KShs) | AMOUNT (KShs)
PUMPS
1.1 | Breaking through the wall of the existing pump house to allow passage of the DN 300mm steel suction pipework to the 3No. Pumps inlet as per specification and indicated on the pump pipework drawing. This will include also the preparation for the existing base plinths for mounting the pumps | Item | LS
Supply and install pipe work, as per drawings, specification and approved by the Engineer, for the pump station. The works shall include jointing the pipes on the surface supported on reinforced concrete piers. The DN 300mm suction pipe from the pumps will feed the DN 800 rising main
1.2 | Straight Specials
Double flanged Steel pipes with the accompanying jointing
1.2.1 | DN 300 PN 16 Pipe | m | 25 |  | 0
Double flanged Steel Pipes or Plain Ended steel pipes with Puddle flanges (Location of Puddle Flange Varies)
1.2.2 | DN 300 PN 16, 1.5m long | Nr | 3 |  | 0
1.3 | Bends
1.3.1 | Nominal Bore 300, steel plain ended bends with provision for couplings for jointing.
1.3.1.1 | 45⁰ DN 300, PN 16 | nr | 10 |  | 0
1.4 | Tapers
All Flanged Concentric Tapers
1.4.1 | DN 500 x DN 300, PN 16 | nr | 1 |  | 0
1.4.2 | DN 800 x DN 500, PN 16 | nr | 1 |  | 0
1.5 | Valves and Penstocks
1.5.1 | Flanged Gate Valve
1.5.1.1 | DN 300, PN 16 with handwheel | nr | 3 |  | 0
1.6 | Non Returrn Valve
1.6.1 | Supply and install a Nominal bore 300mm non return valve approved by the Engineer. Rate to include all jointing/fittings materials. | nr | 3 |  | 0
1.7 | Supply and install a dismantling joint for the Nominal bore DN 300mm for the pump suction pipeline as directed and aproved by the engineer | nr | 6 |  | 0
1.8 | Supply and install pressure gauge for the pump suction pipe as directed and approved by the engineer | nr | 3 |  | 0
1.9 | Provide, Suppy, Install and Commision Water Supply Pumps feeding the DN 800mm, 29km rising main from Baricho Water Works to Kakuyuni reservoir. The pump will be vertical turbine submersible pump drawing water from an existing 3,000 m3 sump tank (Q=700 m3/h, H =100 m). The pump rated at 239.26kW with nominal speed of 1493rpm discharge pipe is a DN 300. Three units required (2 duty, 1 standby) | nr | 3
PAGE TOTAL CARRIED TO COLECTION PAGE
ITEM NO. | DESCRIPTION | UNIT | QTY | RATE (KShs) | AMOUNT (KShs)
1.1 | Allow Sum for a set of Bladder Surge Tank with a capacity of 20 m3, Inlet pipe diameter of 500mm, height 5m and diameter 2m complete with their compressors and accompanying electrical works e.t.c as identified and directed by the Resident Engineer and approved by the Project Manager | nr | 1
1.11 | Supply and install a Nominal bore 300mm pressure regulating valve approved by the Engineer. Rate to include all jointing/fittings materials. | nr | 3
ELECTRICAL WOKS
2 | POWER SUPPLY
2.1 | Supply and install and commision Ground mounted 33/433V 50Hz, 2000kVA transformer with all necessary accessories and fittings according to the specifications. | Sum | 1 |  | 0
3 | POWER DISTRIBUTION
400/1000 volts grade PVC/SWA/PVC copper cable to BS 5467/ IEC 60502 including cable glands, lugs and all accessories
3.1 | Incoming cables of size 2x 4Core 300mm sq PVC/SWA/PVC CU cable from the 2MVA transformer laid in the cable trench and terminated onto the low voltage switchboard to be complete with termination accessories I.e lugs and soldering etc | m | 40 |  | 0
3.2 | Multi-core 2x4C 120mm2 PVC/SWA/PVC armoured copper cable in conduit/floor ducts from main switch board to the 800A TP&N breaker for pumpset control panel .Complete with all the associates civil works | m | 70 |  | 0
3.3 | Multi-core 2x4C 120mm2 PVC/SWA/PVC armoured spaced copper cable in conduit/floor ducts from pump VFD starter to the motor terminal. Complete with all the associates civil works | m | 40 |  | 0
4 | MAIN SWITCHBOARD
4.1 | Main Switchboard, Supply, install, and test and commission 400 volts, metal clad floor mounted type, and Main LV and Instrumentation Panel complete with, instrumentation, integral mains phase failure panel and motorised breakers, status indicators and all accessories. 2,000Amps TP & N rated busbars at full load integrated using 2000Amps TP&N minimum SCR 20kA MCCB adjustable incomer and the following outgoing breakers (20kA MCCB) 3 No. TPN 800Amps. The board is to be fabricated using a minimum of 16 SWG or 2mm thick Galvanised steel sheets. The intrumentation panel will comprise : 1 No. flush ac voltmeter size 95x95mm, 0-500 V ac c/w selector switch and HRC protection fuses; 1 No. flush ac meters size 95x95mm, 0-600 Amps c/w CTS rated 15VA, 600/5 Amps. Integral automatically switched 600 kvar PFC bank, to IP20, comprising dry type capacitors type VARPLUS from MERLIN GERIN Rectiphase, complying to IEC 831 Standards, switched in steps of 1x50, 2x5 kvar complete with all necessary protections , controls, cabling and instrumentations. To have a digital indicator panel. The design of the board must be submitted to the Engineer for approval before fabrication. | LS | 1 |  | 0
| PAGE TOTAL CARRIED TO COLECTION PAGE |  |  |  | 0
ITEM NO. | DESCRIPTION | UNIT | QTY | RATE (KShs) | AMOUNT (KShs)
5 | PUMP CONTROL BOARD
5.1 | Booster pump control panel as per specifications to serve the 3No. pumps on the basis of 2 duty and 1 standby. This will be done as specifications and as directed and approved by the Engineer. Each pump shall have a VFD starter rated at 600Amps TPN minimum SCR 20kA within integrated controls and protection.The protection shall at the very minimum include phase fault, phase failure relay, thermal over load, overcurrent protection,earth leakage and dry run protection. The protection settings shall be to the latest standards of BS or IEC standards. The panels shall also have run hour, ammeter and voltmeter meter for each pump prominently displayed at the front face. The board shall be designed for automatic operation but with an overide to allow manual selection of pumps. The panel shall have automatic step power factor correction capacitors to ensure at no time is the power factor below 0.93. The controls shall use float or pressure switches to achieve start stop operations for the pumps. The panel shall have an audible alarm that sounds whenever there is an electrical fault. The panel shall also have bulbs at the front of the panel illuminating for each pump. The lamps shall be green for pump running, red for pump tripped and amber when pump is not on running but available for duty. Additionally the panel shall be fitted with selector switch to enable the operator to physically select the duty pumps while at the same time retaining the automatic rotational selection capacity to ensure uniform run hours. Each pumpset shall be fitted with an emergency switch adjacent to it to enable immediate stop and another emergency stop button at the panel. | Set | 1 |  | 0
5.2 | Supply and install Instrumentation, Control System and Local SCADA system for operation and management for process monitoring and automation. The syetm to be have user interface and to be able to monitor water levels on the storage tanks at Kakuyuni. | L.sum | 1 |  | 0
5.3 | Provide for the high and medium voltage reorganization and associate works | Sum | 1 |  | 0
5.4 | Provide for civil works for the 2MVA transformer and the 2MVA AVR | Lot | 1 |  | 0
PAGE TOTAL CARRIED TO COLECTION PAGE
BILL 04 Collection Page
| Page 1 |  |  |  | 0
| Page 2 |  |  |  | 0
| Page 3 |  |  |  | 0
BILL 4 COLLECTION CARRIED TO GRAND SUMMARY