## Bill 1 - P&G
IMPROVEMENT OF DRINKING WATER AND SANITATION SYSTEMS IN MOMBASA: MWACHE CKE 1103
LOT 1: CONSTRUCTION OF THE MWACHE TWIN TRUNK MAIN (TM1), SOUTH MAINLAND TRANSMISSION PIPELINE AND DONGO KUNDU RESERVOIR
BID No. CWWDA/AFD/PQ/W4/2022-2023
BILL No. 1 - PRELIMINARIES AND GENERAL ITEMS
ITEM No. | DESCRIPTION | UNIT | QUANTITY | RATE (Kshs) | AMOUNT (Kshs)
CLASS A - GENERAL ITEMS
Contractual Requirements
A110.1 | Perfomance Security | Item | L.S
A110.2 | Environmental, Social, Health and Safety (ESHS) Performance Security. | Item | L.S
A120.1 | Insurance for Works and Contractor's Equipment | Item | L.S
A120.2 | Insurance for Contractor's Personnel | Item | L.S
A120.3 | Insurance against Injury to Third Party Persons and Damage to Property. | Item | L.S
Specified Requirements
A211 | Maintenance and Attendance to the Resident Engineer's Office as per Clause 703 of Particular Specifications including supply of provisions and consumables (stationery, refreshments, cleaning materials, etc) and payment of bills (water, electricity, day and night security, etc). | month | 28
A221 | Provide temporary Supervision Vehicles for use by Resident Engineer's Staff whilst the Project Vehicles under items A422.1 and A422.2 are being procured. The temporary vehicles to be of equivalent specifications to the Vehicles being procured. | km | 10000
A233.1 | Provision of Survey Equipment for sole use by the Resident Engineer for the duration of the Contract (2Nr Total Stations, 2Nr Automatic Levels, 4Nr Metric Levelling Staffs, 15Nr 3m Ranging Rods and other equipment as per Specifications). All equipment shall be new and with carry cases, tripods, reflectors as necessary. All manuals in English Language and metric units. Equipment to revert to Contractor at the end of the Contract. | month | 28
A233.2 | Maintenance of Survey Equipment provided above. | month | 28 |  | 0
A233.3 | Test Running of the Works: Contractor to Test-run the newly constructed facilities for a period of 12 weeks upon completion of the Works. Test Running to be carried out in close liaison with the Employer's Staff. The Contractor to allow for provision of Tools, Conyractor's Personnel, etc, and ensure that the operations are carried out full time on a 24 hour basis. Costs related to "on-job training" of Employer's staff during the Test-Rinning are included in Item A429.8 of this Bill | Item | L.S |  | 0
A233.4 | Allow for provision of As-Built Drawings in accordance with Clause 501 of Particular Specifications. | Item | L.S
A233.5 | Allow for provision of Operation and Maintenance (O&M) Manuals in accordance with Clause 502 of Particular Specifications. | Item | L.S
PAGE TOTAL CARRIED TO COLLECTION SHEET
Attendance upon Resident Engineer's Staff
A241 | Staff for Employer / Engineer (salaries for staff under this item will be based on the latest Job Group Salary Scales for the Government of Kenya's Civil Service including Basic pay, overtime, hardship allowance, house allowance, per diems and other allowances). The Bidder should allow for annual increments in his rates. The rates for the following staff shall consider Kwale County as a primary place of work (Chap. 0110, Clause 8.2.1)
A241.1 | Drivers - 6Nr for 28 months (Government of Kenya Job Group 'J') | MM | 168
A241.2 | Secretary - 1Nr for 28 months (Government of Kenya Job Group 'N') | MM | 28
A241.3 | Office Assistant - 1Nr. for 28 months (Government of Kenya Job Group 'H') | MM | 28
A242.1 | Surveyors - 2Nr. for 28 months (Government of Kenya Job Group 'P') | MM | 56
A242.2 | Chainmen - 2Nr. for 28 months (Government of Kenya Job Group 'G') | MM | 56
A242.3 | ACAD Technician - 1Nr. for 28 months (Government of Kenya Job Group 'M') | MM | 28
A242.4 | Sociologists - 2Nr. for 28 months (Government of Kenya Job Group 'P') | MM | 56
A242.5 | Environmental, Social, Health and Safety (ESHS) Officer - 1Nr. for 28 months (Government of Kenya Job Group 'P') | MM | 28
Testing of Materials and Works
A250.1 | Allow for testing of materials as per Specifications | Item | L.S
A260.1 | Allow for testing of the Works as per Specifications | Item | L.S
Project Signboards
A279 | Provision, fixing, maintaining and removal of Project Signboards. | Nr | 4
Surveying and Setting Out
Allow for Establishment of Level Datum, Topographical Survey, preparation of an updated Layout Plans with Contours at 1m interval, submission of Survey Drawings to the Resident Engineer and Setting Out of proposed Structures and Pipelines.
A290.1 | Water Storage Reservoir Site | ha | 5
A290.2 | Pipeline Routes | m | 35000
PAGE TOTAL CARRIED TO COLLECTION SHEET
Contractor's Camps, Offices, Stores, etc.
A310 | Establish, maintain and remove Contractor's Camp(s) including offices, stores, laboratories, cabins, canteens etc as the Contractor may require and all services inclusing electricity, water, security, transport, staff welfare etc (NB- The Employer has no land available for these Contractor's facilities. Identification and aquisition of suitable locations will be responsibility of the Contractor subject to the Engineer's Approval). | Item | L.S
A4 | Provisional Sums
A41 | Daywork
A410.1 | Provisional Sum for undertaking works under the Dayworks Bill as instructed by the Engineer (Bidder to insert total of Daywork Bill from the Dayworks Summary). | Item | P.S
A410.2 | % Adjustment to the provisional sum for Item A410.1 | %
A421 | Furnishing and Equiping of the Chief Resident Engineer's Office
Note: The Administration Building to be constructed at the Dongo Kundu Reservoir Site will be used as the Chief Resident Engineer's Office for the duration of the Construction and Defects Liability Period.
A421.1 | Provisional Sum for provision of Rented or Pre-fab Offices for Chief Resident Engineer's Staff during the first 16 Weeks of the Contract Period as per Clause 701 of the Particular Specifications. Offices to include 3 Nr Offices, Conference Room, Tea Room, W.C and Parking Space for at least 3 Nr Vehicles. Include for provision of 24 hour security, water, sewerage, electricity, etc. Note: If Construction of the Adminstration Building under Bill No. 4.3 is delayed beyond the first 16 weeks of the Contract Period, the Contractor shall be liable to provide rented or Pre-fab offices for any additional period at his own cost | Item | P.S |  | 1500000
A421.2 | Provisional Sum for furnishing and equiping the R.E's offices to include furniture, computers, digital cameras, printers etc. (List of items to be provided by the Resident Engineer). | Item | P.S |  | 5000000
A421.3 | Provisional Sum for provision of 3Nr. Autodesk Civil 3D Software Single User Three Year Subscription Licenses for exclusive use by the Resident Engineer's staff | Item | P.S |  | 1200000
A421.4 | % Adjustment to the provisional sum for Item A421.1 and A421.2 | % | 7700000
A422 | Project Supervision Vehicles
A422.1 | Provisional Sum for purchase of 4Nr. Double Cabin Pick-up Vehicles (2800cc) for use by Resident Engineer's Staff. Specifications to be approved by the Engineer. Vehicles to revert to the Employer at the end of the Contract. | Item | P.S |  | 34000000
A422.2 | Provisional Sum for purchase of 2Nr Station Wagon Vehicles (2800cc) for use by the Chief Resident Engineer (1Nr) and by the Engineer / Employer (1Nr). Vehicles to revert to the Employer on at the end of the Contract. | Item | P.S |  | 20000000
A422.3 | Provisional Sum for provision of Comprehensive Insurance Cover for the Project Vehicles above for 3 years up to end of Defects Liability Period. | Item | P.S |  | 6500000
PAGE TOTAL CARRIED TO COLLECTION SHEET
A422.4 | Provisional Sum for Running and Maintenance costs of the Project Vehicles including costs of transfer to the Employer at the end of the Contract. | Item | P.S |  | 20000000
A422.5 | % Adjustment to the provisional sum for Items A422.1 to A422.4 | % | 80500000
A423 | Accomodation for the Supervision Staff
A423.1 | Provisional Sum for provision of fully furnished rented accomodation for the Chief Resident Engineer and his Staff, including provision of water, electricity, security, etc. | Item | P.S |  | 22500000
A423.2 | % Adjustment to the provisional sum for Item A423.1 | % | 22500000
A429 | Other Provisional Sums
A429.1 | Provisional Sum for fees requested by various authorities, road agencies, etc for permits and relocation of services. | Item | P.S |  | 10000000
A429.2 | % Adjustment to the provisional sum for Item A429.1 | % | 10000000
A429.3 | Provisional Sum for communication costs (telephone, email, postal, courier services, etc) for the Resident Engineer's Office and Staff. | Item | P.S |  | 3000000
A429.4 | % Adjustment to the provisional sum for Item A429.3 | % | 3000000
A429.5 | Provisional Sum for Inspection and Witness Testing of Pipes, Fittings and other Equipment at manufacturer's premises by the Employer, Engineer and their representatives to be expended as directed by the Engineer. | Item | P.S |  | 5000000
A429.6 | Provisional Sum for Third Party Inspection of Pipes, Fittings, Equipment, etc. during Manufacture and Construction Works to be expended as directed by the Engineer. | Item | P.S |  | 2000000
A429.7 | % Adjustment to the provisional sum Items A429.5 and A429.6 | % | 7000000
A429.8 | Provisional Sum for Training of the Employer's Staff during Construction, Testing and Commissioning of the Works. | Item | P.S |  | 1000000
A429.9 | Provisional Sum to cover costs for Employer's Counterpart Staff assigned to the Project. | Item | P.S |  | 10000000
A429.10 | Provisional Sum to be spent for other Project related expenses as directed by the Engineer / Employer. | Item | P.S |  | 5000000
A429.11 | % Adjustment to the provisional sum Items A429.8 to A429.10 | % | 16000000
PAGE TOTAL CARRIED TO COLLECTION SHEET
A9 | Method Related Charges, Other Items, Works / Obligations
A911 | In addition to the items listed above, tenderer may insert such items as he may require to cover items of work relating to his intended method of executing the works, other obligations as mentioned in the Conditions of Contract, Specifications, etc., costs of which are not to be considered as allowed in the rates and prices for the other items. Full descrition of such Items and Works should be made. If no separate charge is made hereunder, the rates in the Bills of Quantities will be deemed as covering expenses for all such Items and Works.
(Tenderer can include additional sheets of paper if necessary)
i)
ii)
iii)
iv)
ESHS | Environmental, Social, Health and Safety (ESHS) Cost Schedule
ESHS 1 | Resources allocated to ESHS Management (Ref. Clause 4 of ESHS Specifications). | Item | L.S
ESHS 2 | Drafting and updating the ESHS Documentation, Reporting, Inspections (Ref. Clauses 1, 2, 3, 5, 6, 7and 9 of ESHS Specifications). [Note: Cost of ESHS 1 should exclude all or part of the costs of these Tasks] | Item | L.S
ESHS 3 | Implementation of the Health and Safety Plan: Meetings, health care centre, medical check‑ups, emergencies and evacuations, safety protective equipment, hygiene (Ref. Clauses 1, 9, 21 to 25, 27 to 35, 37 and 38 of ESHS Specifications). [Note: Cost of ESHS 1 should exclude all or part of the costs of these Tasks] | Item | L.S
ESHS 4 | Accommodation, Drinking Water, Meals and Transportation of Staff. (Ref. Clauses 36, 40 and 41 of ESHS Specifications). [Note: The Bidder shall detail the financial conditions of the supply of accommodation, meals and transport to its staff. The cost for "Site Mobilization" should exclude all or part of the costs of these Tasks]
ESHS 4.1 | Accommodation | Month | 24
ESHS 4.2 | Meals | Month | 24
ESHS 4.3 | Transport | Month | 24
PAGE TOTAL CARRIED TO COLLECTION SHEET
ESHS 5 | Training and Local Recruitment Management Costs (Ref. Clauses 8 and 39 of ESHS Specifications) [Note: Cost of ESHS 1 should exclude all or part of the costs of these Tasks] | Item | L.S
ESHS 6 | Protection of Adjacent Areas, Biodiversity, Prevention of Erosion and Wastewater Management (Ref. Clauses 10, 11, 12, 17 and 18 of ESHS Specifications). | Item | L.S
ESHS 7 | Traffic, Noise and Atmospheric Emissions Management, Land Take (Ref. Clauses 13, 14, 42, 43 and 44 of ESHS Specifications). | Item | L.S
ESHS 8 | Waste Management (Ref. Clause 15 of ESHS Specifications). | Item | L.S
ESHS 9 | Vegetation Clearing and Site Rehabilitation (Ref. Clauses 16, 19 and 20 of ESHS Specifications). [Note: The cost for "Site Mobilization" should exclude all or part of the costs associated to these Tasks] | Item | L.S
Security | Security Cost Schedule
Security 1 | Security Organisation (Ref. Security Specifications, Article 4.1). | Item | L.S
Security 2 | Travel within the country and to the relevant area (Ref. Security Specifications, Article 4.2). | Item | L.S
Security 3 | Accommodation during assignments (Ref. Security Specifications, Article 4.3). | Item | L.S
Security 4 | Accommodation and security on project sites and worksites (Ref. Security Specifications, Article 4.4). | Item | L.S
Security 5 | Communication (Ref. Security Specifications, Article 4.5). | Item | L.S
Other | This price may remunerate all the other services described in Articles 1 to 3 of the Security Specifications (Ref. Security Specifications, Articles 1 to 3, and 5 to 6). | Item | L.S
PAGE TOTAL CARRIED TO COLLECTION SHEET

## Collection Sheet -Bill No. 1
IMPROVEMENT OF DRINKING WATER AND SANITATION SYSTEMS IN MOMBASA: MWACHE CKE 1103
LOT 1: CONSTRUCTION OF THE MWACHE TWIN TRUNK MAIN (SECTION 1), SOUTH MAINLAND TRANSMISSION PIPELINE AND DONGO KUNDU RESERVOIR
BID No. CWWDA/AFD/PQ/W4/2022-2023
BILL No. 1 - PRELIMINARIES AND GENERAL ITEMS
Amount
(Kshs.)
Page Total, Page 1 of 6
Page Total, Page 2 of 6
Page Total, Page 3 of 6
Page Total, Page 4 of 6
Page Total, Page 5 of 6
Page Total, Page 6 of 6
Bill Total (Exclusive of Value Added Tax - VAT) carried to the Bills of Quantities Grand Summary

## Dayworks
IMPROVEMENT OF DRINKING WATER AND SANITATION SYSTEMS IN MOMBASA: MWACHE CKE 1103
LOT 1: CONSTRUCTION OF THE MWACHE TWIN TRUNK MAIN (TM1), SOUTH MAINLAND TRANSMISSION PIPELINE AND DONGO KUNDU RESERVOIR
BID No. CWWDA/AFD/PQ/W4/2022-2023
SCHEDULE OF DAYWORK RATES
ITEM | DESCRIPTION | UNIT | QUANTITY | RATE | AMOUNT
No. |  |  |  | (KShs.) | (KShs.)
1 | LABOUR
The rates inserted herein should include for all costs such as insurance, travelling time, overtime, accommodation, use and maintenance of small tools of trade and supervision. Only time engaged upon work will be paid for:
1.1 | Unskilled Labourer | Hrs | 100
1.2 | Timberman | Hrs | 50
1.3 | Stone Mason | Hrs | 100
1.4 | Carpenter | Hrs | 50
1.5 | Concreter | Hrs | 50
1.6 | Blaster (Certified) | Hrs | 10
1.7 | Plant Operator | Hrs | 100
1.8 | Pipe Fitter | Hrs | 100
1.9 | Electrician | Hrs | 100
1.1 | Painter | Hrs | 10
1.11 | Welder | Hrs | 100
1.12 | Surveyor | Hrs | 50
1.13 | Chainman | Hrs | 50
1.14 | Foreman | Hrs | 100
1.15 | Watchman (including use of firewood, lights, day, night, Sunday and Public Holiday watching) | Hrs | 50
TOTAL FOR DAYWORK: LABOUR CARRIED FORWARD TO DAYWORK SUMMARY
2 | PLANT
The rates inserted herein should include for all operational and maintenance costs, fuel, oil, grease, operators, turnboys and supervision. Only the time actually employed on works will be paid for and the rates should include for idle, travelling and overtime
2.1 | Compressor (3.0 m3/minute) | Hrs | 100
2.2 | Generator (15 KVA) | Hrs | 100
2.3 | Backhoe Excavator | Hrs | 100
2.4 | Excavator (0.75m3 bucket) with 1.5 Tonne Hammer | Hrs | 100
2.5 | Concrete Vibrator (Petrol or Diesel) - 40mm | Hrs | 100
2.6 | Concrete Mixer - 1.0m3 | Hrs | 100
2.7 | Dumper 0.75m3 | Hrs | 50
2.8 | D7 Bulldozer | Hrs | 100
2.9 | Tandem 3 wheels roller. Dead weight 9 tonnes | Hrs | 50
2.1 | Mobile Crane - 30T | Hrs | 100
2.11 | 5 Tonne Lorry (Tipper) | Hrs | 50
2.12 | 10 Tonne Lorry (Tipper) | Hrs | 50
2.13 | Portable water pump 100mm diameter (inclusive of hoses, couplings, etc.) | Hrs | 50
2.14 | Oxy-Acetylene cutting and welding set, including oxygen and acetylene | Hrs | 20
2.15 | Electric welding set including electrodes | Hrs | 10
TOTAL FOR DAYWORK: PLANT CARRIED FORWARD TO DAYWORK SUMMARY
3 | MATERIALS
All materials are to comply with the specifications. The rates inserted herein are to include for delivery to site, storage and handling.
3.1 | Ordinary Portland Cement | Tonne | 1
3.2 | Mild steel (any size from 8mm to 25mm dia.) | Kg | 50
3.3 | High tensile steel (any size from 8mm to 25mm dia.) | Kg | 50
3.4 | Fine aggregate for concrete | m3 | 20
3.5 | Coarse aggregate for concrete | m3 | 20
3.6 | Shuttering timber | m2 | 10
3.7 | Hardcore | m3 | 50
3.8 | Murram / Gravel | m3 | 50
3.9 | 150mm thick Stone / Concrete Blocks | Nr | 500
3.1 | 225mm thick Stone / Concrete Blocks | m | 500
3.11 | 300mm dia. Concrete Ogee Pipe | m | 20
3.12 | Concrete Class 15/20 | m3 | 10
3.13 | Concrete Class 20/20 | m3 | 10
3.14 | Concrete Class 25/20 | m3 | 10
TOTAL FOR DAYWORK: MATERIALS CARRIED FORWARD TO DAYWORK SUMMARY
DAYWORK SUMMARY
Description |  | Amount in Kshs.
1 | Total For Daywork: Labour
2 | Total For Daywork: Plant
3 | Total for Daywork: Materials
Total for Daywork (Provisional Sum) carried to Bill No. 1 (Preliminaries and General), Item No. A410.1

## Lot 1 Bill 2 Instructions
IMPROVEMENT OF DRINKING WATER AND SANITATION SYSTEMS IN MOMBASA: MWACHE CKE 1103
LOT 1; CONSTRUCTION OF THE MWACHE TWIN TRUNK MAIN (TM1), SOUTH MAINLAND TRANSMISSION PIPELINE AND DONGO KUNDU RESERVOIR
BID No. CWWDA/AFD/PQ/W4/2022-2023
BILL No. 2 - TWIN TRUNK MAIN SECTION 1 (LINE TM1)
INSTRUCTIONS TO BIDDERS
IMPORTANT:
THE BIDDER TO QUOTE FOR ANY ONE OF THE FOLLOWING OPTIONS FOR PIPES AND FITTINGS MATERIALS AND JOINTING. THE SELECTED OPTION TO BE TICKED IN THE SPACE PROVIDED.
SCADA ITEMS ARE NOT INCLUDED - TO BE PROVIDED LATER BY ARTELIA
OPTION | DESCRIPTION | INDICATE SELECTED OPTION BY TICKING ONE BOX BELOW
OPTION 1 | Ductile Iron Socket and Spigot Pipes and Fittings with Standard Push-On Joints as specified |  | `
OPTION 2 | Steel Pipes and Fittings with provision for Field Butt Welded Joints as specified.
ONLY ONE OPTION SHOULD BE SELECTED (TICK ONLY ONE BOX) IF NONE OR BOTH BOXES ARE TICKED, THE BID WILL BE CONSIDERED UNRESPONSIVE AND REJECTED

## Lot 1-Bill 2.1
IMPROVEMENT OF DRINKING WATER AND SANITATION SYSTEMS IN MOMBASA: MWACHE CKE 1103
LOT 1: CONSTRUCTION OF THE MWACHE TWIN TRUNK MAIN (TM1), SOUTH MAINLAND TRANSMISSION PIPELINE AND DONGO KUNDU RESERVOIR
BID No. CWWDA/AFD/PQ/W4/2022-2023
BILL No. 2.1 - TWIN TRUNK MAIN SECTION 1 (LINE TM1)
SUPPLY OF PIPES, FITTINGS, VALVES AND ANCILLARIES
ITEM No. | DESCRIPTION | UNIT | QUANTITY | RATE (Kshs) | AMOUNT (Kshs)
NOTES:
1. | THIS BILL ONLY COVERS RATES FOR PROCUREMENT OF PIPES AND FITTINGS, TRANSPORT TO CONTRACTOR'S SITE STORE AND STORAGE. ALL RATES SHALL INCLUDE SUPPLY OF ALL REQUIRED JOINTING MATERIALS, BOLTS, NUTS, GASKETS, ETC.
2. | RATES FOR TRANSPORT FROM SITE STORE AND INSTALLATION TO BE INCLUDED IN BILL No. 2.2.
3. | BIDDER TO PRICE EITHER FOR STEEL PIPES AND FITTINGS WITH PROVISION FOR FIELD BUTT-WELDED JOINTS AS SPECIFIED OR DUCTILE IRON SOCKET AND SPIGOT PIPES AND FITTINGS WITH STANDARD PUSH-ON JOINTS AS SPECIFIED
4. | ALL RATES TO BE INCLUSIVE OF RELEVANT GOVERNMENT OF KENYA DUTIES AND TAXES, EXCEPT VALUE ADDED TAX (VAT) WHICH IS TO BE ADDED SEPARATELY IN THE GRAND SUMMARY.
5. | ALL PIPES AND FITTINGS TO PRESSURE RATING AS INDICATED FOR EACH ITEM UNLESS OTHERWISE STATED
6. | FOR STEEL PIPELINES, STEEL GRADE AND THICKNESS AS SPECIFIED
7. | PIPELINE EXTERNAL COATING AND INTERNAL LINING AS SPECIFIED FOR THE SELECTED PIPELINE MATERIAL
8. | BIDDERS QUOTING FOR DUCTILE IRON PIPES AND FITTINGS TO PRICE FOR SERIES X ITEMS : OTHER PRICES FOR DUCTILE IRON PIPES AND FITTINGS
9. | IN VIEW OF THE LARGE PIPE DIAMETERS INVOLVED, BIDDERS TO ALLOW FOR REINFORCEMENT OF FITTINGS AS MAYBE REQUIRED, ALL AS PER THE AWWA MANUAL OF WATER SUPPLY PRACTICES (AWWA M11); REINFORCEMENT OF PIPE FITTINGS EITHER BY COLLAR PLATE, WRAPPER PLATE OR BY CROTCH-PLATE, AS MAY BE REQUIRED. BIDDER TO INCLUDE RATE FOR REINFORCEMENT OF FITTINGS IN THEIR RATES FOR RESPECTIVE FITTINGS
CLASS I: PIPE WORK - PIPES
I4 | Ductile Iron Pipes or Steel Pipes; Joints as specified
Ductile Iron Socket and Spigot Pipes with Standard Push-On Joints (class 25, cement mortar lining, zinc-aluminium coating) OR Steel Pipes with provision for Field Butt-Welded Joints (minimum yield strength 290 Mpa, minimum wall thickness 8.8mm, epoxy lining, 3-layer polyethylene coating)
I45 | DN 1000 mm | m | 3075
PAGE TOTAL CARRIED TO BILL COLLECTION SHEET
I5 | High Density Polyethylene Pipes (HDPE)
Butt-fusion weld jointed HDPE Pipes - PN 16
I51 | Nominal Bore 110 mm (provisional length) for Chamber Drainage | m | 200
I52 | Nominal Bore 225 mm (provisional length) for Washout Drainage | m | 500
CLASS J: PIPE WORK - FITTINGS AND VALVES
J3 | Ductile Iron Fittings or Steel Fittings; Joints as specified
J31 | Bends
J311 | Nominal Bore 200mm; Ductile Iron Socket and Spigot or Double Socketed Bends OR Steel Socket and Spigot Bends
J311.1 | 90⁰ DN 200, PN 16 (provisional) | Nr | 10
J315 | Nominal Bore 1000mm; Ductile Iron Socket and Spigot or Double Socketed Bends with Standard Push-On Joints OR Steel plain ended Bends with provision for field butt-welded Joints
J315.1 | 11.25⁰ DN 1000, PN 16 | Nr | 44
J315.2 | 22.5⁰ DN 1000, PN 16 | Nr | 11
J32 | Junctions and Branches
All Flanged Tee
J325 | Nominal Bore 1000mm
J325.1.1 | DN 1000 x DN 200, PN 16 all Flanged Tee for Air Valves within Line Valve Chambers | Nr | 2
J325.1.2 | DN 1000 x DN 800, PN 16 all Flanged Tee for Air Valves | Nr | 12
J325.1.3 | DN 1000 x DN 1000, PN 16 all Flanged Tee for offtakes | Nr | 2
All Flanged Level Invert Tee
J325.2.1 | DN 1000 x DN 200, PN 16 all Flanged Tee for Washouts | Nr | 11
J34 | Ferrous Couplings
J341.1 | DN 200, PN 16 - Stepped Coupling | Nr | 11
J345.1 | DN 1000, PN 16 - Straight Coupling (Provisional) | Nr | 3
J35 | Ferrous Flange Adaptor
J351.1 | DN 200 PN 16 | Nr | 11
J355.1 | DN 1000, PN 16 | Nr | 1
J38 | Straight Specials
Plain Ended Pipes with Puddle Flanges (location of Puddle Flange as specified in Drawings)
J381.1 | DN 200, PN 16, 1.2m long (Provisional) | Nr | 5
Plain Ended Pipes without Puddle Flanges
J381.2 | DN 200, PN 16, 1.2m long | Nr | 11
PAGE TOTAL CARRIED TO BILL COLLECTION SHEET
Double Flanged Pipes without Puddle Flanges
J385.1 | DN 1000, PN 16, 3m long | Nr | 12
J385.2 | DN 1000, PN 16, 6m long | Nr | 9
Flanged Spigot Pipes without Puddle Flanges
J385.3 | DN 1000, PN 16, 3m long | Nr | 4
J385.4 | DN 1000, PN 16, 1.5m long | Nr | 21
Flanged Spigot Pipes with Puddle Flanges (location of Puddle Flange as specified in Drawings)
J385.5 | DN 1000, PN 16, 1.5m long with puddle flange | Nr | 23
Double Flanged Pipes with Puddle Flanges (location of Puddle Flange as specified in Drawings)
J385.6 | DN 1000, PN 16, 1.5m long with puddle flange | Nr | 2
Special Fittings
J381.3 | DN 200, PN 16, special double flanged pipe 325mm long with flange to suit 800mm dia. tee on one end and 200mm dia flange on the other end as per Dwg No. M430/SD/02 (Detail 1). | Nr | 12
J385.7 | DN 1000 PN 16 Dismantling Joint (Viking Johnson dismantling joint, nominal length 307mm or approved equivalent) | Nr | 2
J39 | Ferrous Blank Flange
J395.1 | DN 1000 PN 16 | Nr | 1
J8 | Valves and Penstocks
J81 | Flanged Gate Valve
J811.1 | DN 200, PN 16, with handwheel (Isolating Valve for Air Valves) | Nr | 12
J811.2 | DN 200, PN 16, with Extension Spindle, length n.e. 3.0m without handwheel (for washouts) | Nr | 11
J84 | Flanged Butterfly Valve complete with Gear Mechanism designed to slow down flow reduction at end of closure as specified and Hand Wheel as specified
J845.1 | DN 1000, PN 16 | Nr | 1
J86 | Air Valve
J861.1 | Flanged Double Acting Non-Slam (Anti-Surge) Air Valve (DAV) as specified
J861.1 | DN 200, PN 16 | Nr | 12
PAGE TOTAL CARRIED TO BILL COLLECTION SHEET
CLASS X: OTHER COSTS FOR DUCTILE IRON PIPES & FITTINGS
Note: This item is only to be priced if the Bidder has quoted for Ductile Iron Pipes & Fittings. Bidders quoting for Steel Pipes and Fittings should not price this item.
Additional protection for Ductile Iron Pipes and Fittings in areas of high corrosivity
X990.1 | Carry out Field Tests and Analysis to confirm the specified external coating of Ductile Iron Pipes and Fittings or propose an alternative if required at particular locations | m | 3075
Ductile Iron Pipes and Bends with Self-Anchored Joints
X999 | Extra-over cost on top of Items I4 and J31 for the supply of Ductile Iron Pipes and Bends with Self-Anchored Joints
X999.1 | DN 1000mm C25 Ductile Iron pipes with Self-Anchored Joints | m | 100
X991.2 | DN 1000mm C25 Ductile Iron bends with Self-Anchored Joints | Nr | 5
PAGE TOTAL CARRIED TO BILL COLLECTION SHEET

## Collection Sheet L1-Bill 2.1
IMPROVEMENT OF DRINKING WATER AND SANITATION SYSTEMS IN MOMBASA: MWACHE CKE 1103
LOT 1:CONSTRUCTION OF THE MWACHE TWIN TRUNK MAIN (TM1), SOUTH MAINLAND TRANSMISSION PIPELINE AND DONGO KUNDU RESERVOIR
BID No. CWWDA/AFD/PQ/W4/2022-2023
BILL No. 2.1 - TWIN TRUNK MAIN SECTION 1 (LINE TM1)
SUPPLY OF PIPES, FITTINGS, VALVES AND ANCILLARIES
Amount
(Kshs.)
Page Total, Page 1 of 4
Page Total, Page 2 of 4
Page Total, Page 3 of 4
Page Total, Page 4 of 4
Bill No. 2.1 Total Exclusive of VAT carried to Summary Sheet

## Lot 1 -Bill 2.2
IMPROVEMENT OF DRINKING WATER AND SANITATION SYSTEMS IN MOMBASA: MWACHE CKE 1103
LOT 1: CONSTRUCTION OF THE MWACHE TWIN TRUNK MAIN (TM1), SOUTH MAINLAND TRANSMISSION PIPELINE AND DONGO KUNDU RESERVOIR
BID No. CWWDA/AFD/PQ/W4/2022-2023
BILL No. 2.2 - TWIN TRUNK MAIN SECTION 1 (LINE TM1)
PIPELINE CONSTRUCTION
ITEM No. | DESCRIPTION | UNIT | QUANTITY | RATE (Kshs) | AMOUNT (Kshs)
NOTES:
1. | The Mwache Twin Trunk Main traverses through a number of valleys along its entire alignment. A significant section of the pipeline is to be constructed within the Mwache Forest, characterized by a dense thicket and steep cross-fall slopes. The pipeline in this section is to be laid between the Mwache River and the Standard Gauge Railway, with limited motorized acccess due to the steep topography with cross slopes > 1:1 at some sections. The Twin Trunk Main has been designed as a Twin pipeline with the two pipelines to be laid adjacent to each other for the entire length. The Contractors Rates should allow for any specific measures necessary to deal with the terrain, provision of access roads to work sites, liason with the relevant authorities and local residents, including payment of any required Statutory charges that may be levied to the Contractor, etc. The costs for compliance with specific requirements for carrying out the levies shall be deemed to be included in the Contractor's rates. The Contractor will be required to submit a Method Statement for execution of works under these specific conditions for approval prior to execution of the works. These include, but are not limited to the following; i) No blasting will be permitted ii) The contractor to maintain uninterrupted continuity of Water Supply in existing Mains where applicable iii) Pedestrians and Vehicular access to individual Shops/ Plots, Houses, etc. to be maintained at all times. Where necessary, alternative temporary access to be availed iv) Safety hoarding, lighting, bands, warning signs, etc. to be maintained at all times. v) Immediate Reinstatement and Stabilization of Slopes upon laying of the Pipeline
2. | The proposed works are within the Coastal Region, generally charactyerized by a corrosive environment and soils. Bidders quoting for Steel Pipes and Fittings shall be required to price for Cathodic Protection of the entire Transmission Pipeline (Item X995). Installation of the Cathodic Protection System to be carried out by a certified approved Specialized Sub-Contractor.
3. | All Rates to include for Government of Kenya Duties and Taxes, Except Value Added Tax (VAT).
4. | Value Added Tax (VAT) to be added separately in the Grand Summary.
CLASS A: GENERAL ITEM
A260 | Testing of works
Pipeline Testing and Commissioning, including provision of all Equipment, Materials and works necessary for Testing, such as but not limited to thrust blocks, anchor blocks, provision, transportation and use of water, requisite pipe fittings, etc., successful testing to specified pressure and safe disposal of used water.
NOTE: Any additional fittings that may be neccecitated by the Contractor's Methodology for testing shall be supplied and installed at the Contractor's own cost.
PAGE TOTAL CARRIED TO BILL COLLECTION SHEET
A260.1 | DN 1000mm | m | 3075
Disinfection of Pipe lines: Flushing with clear water, filling with water containing 0.05 g/l calcium hypochlorite, left for 24 hours. This includes supply of all necessary equipment, materials, chemicals and water, measurement of residual chlorine, all as specified and safe disposal of disinfecting water to Engineer's approval.
A260.2 | DN 1000 Pipeline | m | 3075
A3 | Method Related Charges
A35 | Temporary Works
A35.1 | Working within available limited wayleave, include costs for double / multiple handling of excavated materials if required, as well as provision of alternative access to private property during execution of the works. | Item | L.S
A35.2 | Working within marshy areas with weak soil formation | Item | L.S
A35.3 | Keeping trenches free of excessive groundwater, seepage or water from whatever source | Item | L.S
A35.4 | Liaison, facilitation with local residents | Item | P.S | 5000000 | 5000000
A35.5 | Allow for carrying out Pilot Excavation, exposing and identification of existing UNDERGROUND SERVICES (water lines, sewerlines, storm water drains, telephone/electricity ducts, fibre optic cables, etc.) prior to setting out and excavation of the pipeline where applicable. Pilot excavation n.e. 3m depth on approx 5m wide corridor, estimate No. of pilot holes along the Pipeline route is 50Nr. | Item | L.S
A35.6 | Allow for crossing existing UNDERGROUND SERVICES (water lines, sewerlines, storm water drains, telephone/electricity ducts, fibre optic cables (including cables for security cameras), etc.), including reinstatement to original states and liason with the relevant body for the inspection/ approval during execution of the works. Nominal bore up to - 1800mm | Item | L.S
A35.7 | Allow a Provisional Sum for re-alignment of existing services, both buried and above ground, as may be required and directed on site, to create space for laying of proposed Transmission Mains. This item covers re-alignment/re-routing of existing water mains, Telecommunication cables, buried and overhead power lines where appropriate. | Item | P.S | 1000000 | 1000000
A35.8 | Allow for any other method related charges the Bidder feels may be required. These should be indicated below with pricing of each item (Bidder may attach additional sheets if necessary):
| i) | Item | L.S
| ii) | Item | L.S
CLASS D: DEMOLITION AND SITE CLEARANCE
D100.1 | General site clearance along easement (including top soil removal, limited to the trench width) | ha | 4.5
D2 | Tree Cutting
Cut down trees, grub up roots and cart away to tips
D210 | Girth: 0.5 m - 1.0 m | Nr | 100
PAGE TOTAL CARRIED TO BILL COLLECTION SHEET
D220 | Girth: 1.0 m - 2 m | Nr | 200
D230 | Girth 2.0 m - 3 m | Nr | 500
D240 | Girth 3.0 m - 5 m | Nr | 200
D320 | Remove stump dia. 0.5 - 1m | Nr | 100
D330 | Remove stump dia. exceeding 1m | Nr | 100
CLASS E: EARTHWORKS
E220 | Mass Excavation in selected areas to level localized high points and to remove imported deposited material on pipeline alignment to original ground level as directed by the Engineer prior to excavation of pipeline trenches. Include for transportation and disposal of excavated material to approved tips identified by the Contractor in liaison with Local Authorities. | m³ | 2000
CLASS I: PIPE WORK - PIPES
Transport from Site Store, Lay and Joint Pipes in Trench, Include for Excavation, Preparation of Surfaces, Disposal of Excavated Material, Shoring Sides of Excavation and Backfilling.
Note: Trench width and minimum cover to pipes is as per the Specification. The cost shall include for strutting, shuttering, stabilizing the earth faces of trenches and keeping the trenches free of water from whatever source by pumping or other means and cost of use of selected soil from the excavated material for compaction in bed and surround to backfilling of trenches, etc., all as specified.
I4 | Ductile Iron Pipes OR Steel Pipes; Joints as specified
Ductile Iron Socket and Spigot Pipes with Standard Push-On Joints OR Steel Pipes with provision for Field Butt-welded Joints. Rate for Welded Steel Pipe to include for provision of all materials and wrapping of all Welded joints as specified
I45 | Nominal Bore 1000mm in trenches
I451 | Nominal Bore 1000mm not in trenches (For aerial crossings) | m | 77
I452 | Depth not exceeding 1.5 m | m | 56
I453 | Depth 1.5 m - 2.0 m | m | 165
I454 | Depth 2.0 m - 2.5 m | m | 662
I455 | Depth 2.5 m -3.0 m | m | 660
I456 | Depth 3.0 m - 3.5 m | m | 659
I457 | Depth 3.5m - 4.0 m | m | 465
I458 | Depth exceeding 4.0 m | m | 331
I5 | High Density Polyethylene Pipes (HDPE)
I51 | Butt-fusion weld jointed HDPE Pipes - PN 16 Nominal Bore 110mm in trenches
I512 | Depth not exceeding 1.5 m | m | 40
I513 | Depth 1.5m - 2.0 m | m | 100
I514 | Depth 2 m - 2.5 m | m | 100
PAGE TOTAL CARRIED TO BILL COLLECTION SHEET
I52 | Butt-fusion weld jointed HDPE Pipes - PN 16 Nominal Bore 225mm in trenches
I522 | Depth n.e 1.5 | m | 120
I523 | Depth 1.5m - 2.0m | m | 120
I524 | Depth 2.0m - 2.5m | m | 140
I525 | Depth 2.5m - 3.0m | m | 140
I526 | Depth 3.0m - 3.5m | m | 140
I527 | Depth 3.5m - 4.0m | m | 100
I528 | Depth exceeding 4.0m, Maximum depth 6m | m | 100
CLASS J: PIPE WORK - FITTINGS AND VALVES
Transport from Site Store, Lay and Joint Pipes and Fittings in Trench/on Aerial Crossings, Include for Excavation, Preparation of Surfaces, Disposal of Excavated Material, Shoring Sides of Excavation and Backfilling. Rate to include for Transport to Site and Installation of all Jointing Materials, Bolts, Nuts, Gaskets, etc.
J3 | Ductile Iron Fittings OR Steel Fittings; Joints as specified
J31 | Bends
J311.1 | Nominal Bore 200mm; Ductile Iron Socket and Spigot or Double Socketed Bends OR Steel Socket and Spigot Bends
J311.1 | 90⁰ DN 200, PN 16 (provisional) | Nr | 10
J315 | Nominal Bore 1000mm; Ductile Iron Socket and Spigot or Double Socketed Bends with Standard Push-On Joints OR Steel plain ended Bends with provision for field butt-welded Joints
J315.1 | 11.25⁰ DN 1000, PN 16 | Nr | 44
J315.2 | 22.5⁰ DN 1000, PN 16 | Nr | 11
J32 | Junctions and Branches
All Flanged Tee
J325 | Nominal Bore 1000mm
J325.1.1 | DN 1000 x DN 200, PN 16 all Flanged Tee for Air Valves within Line Valve Chambers | Nr | 2
J325.1.2 | DN 1000 x DN 800, PN 16 all Flanged Tee for Air Valves | Nr | 12
J325.1.3 | DN 1000 x DN 1000, PN 16 all Flanged Tee for offtakes | Nr | 2
All flanged Level Invert Tee
J325.2.1 | DN 1000 x DN 200, PN 16 all Flanged Tee for Washout | Nr | 11
J34 | Ferrous Couplings
J341.1 | DN 200, PN 16 - Stepped Coupling | Nr | 11
J345.1 | DN 1000, PN 16- Straight Coupling (Provisional) | Nr | 5
J35 | Ferrous Flange Adaptor
J351.1 | DN 200 PN 16 | Nr | 11
J355 | DN 1000, PN 16 | Nr | 1
PAGE TOTAL CARRIED TO BILL COLLECTION SHEET
J38 | Straight Specials
Plain Ended Pipes with Puddle Flanges (location of Puddle Flange as specified in Drawings)
J381.1 | DN 200, PN 16, 1.2m long (Provisional) | Nr | 3
Plain Ended Pipes without Puddle Flanges
J381.2 | DN 200, PN 16, 1.2m long | Nr | 11
Double Flanged Pipes without Puddle Flanges
J385.1 | DN 1000, PN 16, 3m long | Nr | 12
J385.2 | DN 1000, PN 16, 6m long | Nr | 9
Flanged Spigot Pipes without Puddle Flanges
J385.3 | DN 1000, PN 16, 3m long | Nr | 4
J385.4 | DN 1000, PN 16, 1.5m long | Nr | 21
Flanged Spigot Pipes with Puddle Flanges (location of Puddle Flange as specified in Drawings)
J385.5 | DN 1000, PN 16, 1.5m long with puddle flange | Nr | 23
Double Flanged Pipes with Puddle Flanges (location of Puddle Flange as specified in Drawings)
J385.6 | DN 1000, PN 16, 1.5m long with puddle flange | Nr | 2
Special Fittings
J381.3 | DN 200, PN 16, special double flanged pipe 325mm long with flange to suit 800mm dia. tee on one end and 200mm dia flange on the other end as per Dwg No. M430/SD/02 (Detail 1). | Nr | 12
J385.7 | DN 1000 PN 16 Dismantling Joint (Viking Johnson dismantling joint, nominal length 307mm or approved equivalent) | Nr | 2
J39 | Ferrous Blank Flange
J395.1 | DN 1000 PN 16 | Nr | 1
J8 | Valves and Penstocks
J81 | Flanged Gate Valve
J811.1 | DN 200, PN 16, with handwheel (Isolating Valve for Air Valves) | Nr | 12
J811.2 | DN 200, PN 16, with Extension Spindle, length n.e. 5.0m without handwheel (for washouts) | Nr | 11
J84 | Flanged Butterfly Valve complete with Gear Mechanism designed to slow down flow reduction at end of closure as specified and Hand Wheel as specified
J845.1 | DN 1000, PN 16 | Nr | 1
J86 | Air Valve
J861 | Flanged Double Acting Non-Slam (Anti-surge) Air Valve (DAV) as specified
J861.1 | DN 200, PN 16 | Nr | 12
PAGE TOTAL CARRIED TO BILL COLLECTION SHEET
CLASS K: PIPE WORK - CHAMBERS AND PIPE WORK ANCILLARIES
Chambers, ducts, culverts, crossings, thrust and anchor blocks, reinstatement and others pipeworks and ancillaries.
Note:- Items for Work in this class shall include:- - Excavation, dewatering, preparation of surfaces, disposal of excavated material, shoring sides of excavation, backfilling and removal of redundant services. - Concrete, reinforcement, formwork, joints and finishes. - Tips for disposal of excavated material or debris to be identified by the Contractor in liaison with the Local Authorities. - Rate to include for placing and compaction of pipe embedment material below the chamber and filling around pipe before construction of chamber - All Chambers to be fitted with adequate drainage system and permanent ventilation as per details or as directed by Engineer in Site. - Chambers to be fitted with plastic coated step irons or Access ladders as specified; and lockable covers to access manholes.
K23 | IN SITU CONCRETE CHAMBERS
K232 | Depth 1.5 - 2 m
K232.1 | Provide all materials and construct Reinforced concrete WASHOUT VALVE Chamber, internal dimensions 1200mm x 1200mm. Include for supply and fixing of removable reinforced concrete cover, mild steel frame, lifting / opening mechanism, plastic coated step irons, Vents, drainage system etc . All as specified and as detailed on Drawing No. M430/SD/03 | Nr | 2
K233 | Depth 2-2.5 m
K233.1 | Provide all materials and construct Reinforced Concrete AIR VALVE Chamber, internal dimensions 2400mm x 2000mm. Include for supply and fixing of removable reinforced concrete cover, mild steel frame, lifting / opening mechanism, plastic coated step irons, Vents, drainage system, etc . All as specified and as detailed on Drawing No. M430/SD/02 | Nr | 4
K234 | Depth 2.5-3 m
K234.1 | Provide all materials and construct Reinforced Concrete AIR VALVE Chamber, internal dimensions 2400mm x 2000mm. Include for supply and fixing of removable reinforced concrete cover, mild steel frame, lifting / opening mechanism, plastic coated step irons, Vents, drainage system, etc . All as specified and as detailed on Drawing No. M430/SD/02 | Nr | 2
K234.2 | Provide all materials and construct Reinforced concrete LINE VALVE Chamber, internal dimensions not exceeding 2700mm x 2400mm. Include for supply and fixing of removable reinforced concrete cover, mild steel frame, lifting / opening mechanism, mild steel CAT Ladder, Vents, drainage system etc . All as specified and as detailed on Drawing No. M430/SD/05 | Nr | 1
PAGE TOTAL CARRIED TO BILL COLLECTION SHEET
K235 | Depth 3 - 3.5 m
K235.2 | Provide all materials and construct Reinforced concrete AIR VALVE Chambers, internal dimensions 2400mm x 2000mm. Include for supply and fixing of removable reinforced concrete slab / cover, mild steel frame, lifting / opening mechanism, step irons, compacted granular fill, vents, drainage system, rendering of exposed blockwork etc . All as specified and as detailed on Drawing No. M430/SD/02 | Nr | 1
K236 | Depth 3.5 - 4 m
K236.1 | Provide all materials and construct Reinforced concrete AIR VALVE Chambers, internal dimensions 2400mm x 2000mm. Include for supply and fixing of removable reinforced concrete slab / cover, mild steel frame, lifting / opening mechanism, step irons, compacted granular fill, vents, drainage system, rendering of exposed blockwork etc . All as specified and as detailed on Drawing No. M430/SD/02 | Nr | 1
K237 | Depth exceeding 4 m
K237.1 | Provide all materials and construct Reinforced concrete AIR VALVE Chambers, internal dimensions 2400mm x 2000mm. Include for supply and fixing of removable reinforced concrete slab / cover, mild steel frame, lifting / opening mechanism, step irons, compacted granular fill, vents, drainage system, rendering of exposed blockwork etc . All as specified and as detailed on Drawing No. M430/SD/02 | Nr | 2
K25 | PRECAST CONCRETE CHAMBERS
K254 | Depth 2.5-3m
K254.1 | Provide all materials and construct Precast Concrete WASHOUT VALVE Surface Box. Include for supply and fixing of Class 30 PCC unit, MS surface box and lockable cover, compacted granular fill, OD 160mm uPVC pipe sleeve, length not exceeding 3m, etc. all as specified and as detailed on Drawing . No. M430/SD/04 | Nr | 2
K255 | Depth 3-3.5m
K255.1 | Provide all materials and construct Precast Concrete WASHOUT VALVE Surface Box. Include for supply and fixing of Class 30 PCC unit, MS surface box and lockable cover, compacted granular fill, OD 160mm uPVC pipe sleeve, length not exceeding 3.5m, etc. all as specified and as detailed on Drawing . No. M430/SD/04 | Nr | 1
K256 | Depth 3.5-4m
K256.1 | Provide all materials and construct Precast Concrete WASHOUT VALVE Surface Box. Include for supply and fixing of Class 30 PCC unit, MS surface box and lockable cover, compacted granular fill, OD 160mm uPVC pipe sleeve, length not exceeding 4m, etc. all as specified and as detailed on Drawing . No. M430/SD/04 | Nr | 2
K257 | Depth exceeding 4m
K257.1 | Provide all materials and construct Precast Concrete WASHOUT VALVE Surface Box. Include for supply and fixing of Class 30 PCC unit, MS surface box and lockable cover, compacted granular fill, OD 160mm uPVC pipe sleeve, length exceeding 4m, etc. all as specified and as detailed on Drawing . No. M430/SD/04 | Nr | 3
PAGE TOTAL CARRIED TO BILL COLLECTION SHEET
K6 | CROSSINGS
K63 | Under-River Crossings, Width exceeding 10m
Details as per Dwg No. M430/SD/13
K633 | Pipe Nominal bore 900-1800mm
Note: Items for work shall include:
K633.1 | Excavation for foundation in river/stream beds depth n.e 4.0m, preparation of surfaces, disposal of excavated material, upholding sides of excavation, backfilling and removal of redundant services, all as per Dwg No. M430/SD/10, Nominal Bore 1000mm | m | 140
K633.2 | Extra over item K633.1 for excavation in rock, depth n.e. 4.0m including preparation of trenches (No blasting permitted) (Provisional)
K633.2.1 | Class 'A' | m3 | 15
K633.2.2 | Class 'B' | m3 | 280
K633.2.3 | Class 'C' | m3 | 60
K633.3 | Transport from Site Store, Install, Test and Commission DN 1000mm ferrous pipes on under-river Crossings, jointing to specifications | m | 140
K633.4 | Supply 'Denso Tape' wrapping or approved equivalent. Bidder to include for wrapping at welded joints on the 1000mm dia. ferrous pipe in two layers as directed by the Engineer. | m² | 500
K633.5 | Backfill the trench with concrete Class 15/20 surround, include for vibrating as directed by the Engineer all as per Dwg No. M430/SD/10 | m3 | 100
K633.6 | Backfill the trench with approved selected excavated material compacted in 300mm layers | m3 | 85
K633.7 | Backfill trench with approved imported compacted granular material compacted in 300mm layers | m3 | 95
Gabion Works
K633.8 | Provide all materials and carry out laying of 2m x 1m x 1m Gabions mesh wire minimum size 5mm or as specified. Gabion Boxes to be laid in stretches with 0.5m overlap, mesh wire to be galvanised and minimum diameter 5mm. Include for tying of adjacent gabions with approved wire and 16mm dia anchor rods to suit site conditions (Provisional) | Nr | 400
K633.9 | Provide all materials and carry out laying of 0.23 - 0.5m thick Gabion Mattresses mesh wire minimum size 5mm or as specified , mesh wire to be galvanised and of minimum diameter 5mm. Include for tying of adjacent gabions with approved wire and 16mm dia anchor rods to suit site conditions (Provisional) | m2 | 840
K633.10 | Provide and place rockfill to gabions and mattresses | m3 | 2000
K633.11 | Extra over for infilling of gabions with Class 15 mass concrete | m3 | 40
K633.12 | Formwork
Provide and fix shutterings including propping, strutting and striking, all as specified.
Sawn Formwork - Class F1 Finish
K633.12.1 | Vertical Sides of Concrete in foundation | m2 | 392
PAGE TOTAL CARRIED TO BILL COLLECTION SHEET
K633.13 | Method Related Charges
K633.13.1 | Allow for diverting River/Stream including construction of cofferdam etc., for river crossing works and reinstate after construction. The River/Stream to be kept operational during construction, width 3 - 6m | Nr | 4
K633.13.2 | Allow for keeping excavation free of water which may occur through ground water seepage, rain or other means. | Item | L.S
K633.13.3 | Allow for any other method related charges the Bidder feels may be required. These should be indicated below with pricing of each item.
| i) | Item | L.S
| ii) | Item | L.S
K7 | Reinstatement
K733.3 | Breaking up, temporary and permanent reinstatement of MURRAM road with 300mm thick well graded stabilised gravel with 3% cement base compacted in 150mm thick layers using an 8-10 tonne roller and 150mm deep approved compacted hardcore to the satisfaction of the Engineer. Nominal pipe bore n.e. 1800mm. all as per Dwg No. M430/SD/12. Rates quoted shall be deemed to include for costs incurred on traffic control, signage and safety measures during execution of the works. | m | 20
K743.1 | Breaking up temporary and permanent reinstatement of UNPAVED FOOTPATHS. Pipe bore 900mm - 1800mm all as per Dwg No. M430/SD/12 | m | 10
K8 | Other Pipework Ancillaries
K821 | Marker Posts on Pipeline Alignment
K821.1 | Supply and fix marker posts for water main route, road crossings, change of direction, air valves, washouts, and valve chambers. All in accordance with drawings and specifications | Nr | 100
K822 | Pipeline Wayleave Monumentation
K822.1 | Supply and Install wayleave Boundary Indicator Posts at edges of acquired Pipeline Wayleave, to mark full extent of the pipeline wayleave. Wayleave Boundary Indicator Posts details as per drawings, to be installed at approx. intervals of 200m. | Nr. | 50
Wash-out Outfall Rising Pipe
K87 | Provide all materials, fabricate and install washout chamber outfall rising pipe as detailed in drg. No. M430/SD/03. Rate to include for supply of all fittings, jointing, installation and connection to washout tee and valve. | Nr. | 13
K88 | Removal and Reinstatement of Existing Hedges, Fences, Walls and Drains
K88.1 | Allow for removal of existing HEDGES and reinstating these after laying of the water mains is completed. (Provisional) | m | 50
K88.2 | Allow for breaking up of existing FENCES, including but not limited to chain link fence, barbed wire fence, timber, iron sheet, electric fence, etc., and reinstating these after construction of the water mains is completed. (Provisional) | m | 50
PAGE TOTAL CARRIED TO BILL COLLECTION SHEET
K88.3.1 | Allow for breaking up of existing UNLINED EARTH DRAINS and reinstating these after construction of the water mains is completed. Include for provision of diverting the drains or water ways and keeping them operational during construction. Depth of Drain n.e. 3m (See Drg. No. M430/SD/19) (Provisional) | m | 100
CLASS L:- PIPEWORK - SUPPORTS AND PROTECTION, ANCILLARIES TO LAYING AND EXCAVATION
L1 | Extras to excavation and backfilling (Provisional)
L11 | In pipe trench and chambers
L111.1 | Excavation in trench for rock class "A" | m³ | 400
L111.2 | Excavation in trench for rock class "B" | m³ | 2200
L111.3 | Excavation in trench for rock class "C" | m³ | 1000
Note:- Blasting is NOT permitted for Item L11
L5 | Surrounds
L52 | Provide, transport to site and place selected excavated granular fill and compact in bed and surround to pipes as specified and where directed by the Engineer.
L525 | To pipes nominal bore: 900 - 1200 mm | m | 1850
L53 | Provide, transport to site and place imported granular fill and compact in bed and surround to pipes as specified and where directed by the Engineer.
L535 | To pipes nominal bore: 900 - 1200 mm | m | 1230
L54 | Provide all materials, transport to site and place mass concrete class 15/20 in bed and surround to pipes under road crossings. Include for provision, fixing and dismantling of all formwork, vibration of concrete etc. all as per Dwg No. M430/SD/10
L545 | To pipes nominal bore: ne 900 - 1200 mm | m | 20
L7 | Concrete Support, Thrust Blocks, Stools and Anchor Blocks
Details as per Dwg No. M430/SD/08 - 09 (Provisional)
Rates to include for excavation, formwork, provision and placing of concrete, backfilling etc.
Class 20/20 Mass Concrete
NOTE:- The work includes pipe and fitting fixing
L73 | Volume:- 0.2 - 0.5 m³
L731 | To pipes nominal bore: not exceeding 200mm | Nr
L74 | Volume:- 0.5 - 1 m³
L745 | To pipes nominal bore: 900 -1200mm | Nr | 24
L75 | Volume:- 1 - 2 m³
L755 | To pipes nominal bore: 900 -1200mm | Nr | 14
L76 | Volume:- 2 - 4 m³
L765 | To pipes nominal bore: 900 -1200mm | Nr | 42
L77 | Volume:- 4 - 6 m³
L775 | To pipes nominal bore: 900 -1200mm | Nr | 109
L78.1 | Volume:- 6- 10 m³
L785.1.1 | To pipes nominal bore: 900 -1200mm | Nr | 3
L78.2 | Volume:- exceeding 10m³
L785.1.2 | Volume 50 to 60m3 to pipes nominal bore: 900 -1200mm | Nr | 1
PAGE TOTAL CARRIED TO BILL COLLECTION SHEET
CLASS V: PAINTING
V310 | Allow for cleaning and painting with 3 coats of approved epoxy paint on all exposed Pipework, Fittings, Valves, etc. | m2 | 500
CLASS X: MISCELLANEOUS WORKS
X4 | Gabion Works
X411 | Supply and Install approved Gabion Boxes, size 2m x 1m x 1m mesh wire minimum size 5mm diameter or as specified. Gabion Boxes to be laid in cascading stacks around R.C. piers on aerial crossings, and where instructed by the Engineer on site, all as directed. Rate to include for supply and packing of approved hardcore into gabion boxes, all to Engineer's approval, as shown on Drg. No. M430/SD/10. | Nr | 110
X421 | Ditto - but Gabion Mattresses, thickness 500mm mesh wire 5mm diameter | m2 | 150
X990 | EROSION CONTROL AND PROTECTION MEASURES (PROVISIONAL)
X990.1 | Provide all materials and construct mass concrete EROSION CHECKS on steep sloped as specified and according to details given in Drg. No. M430/SD/10. | Nr. | 110
X990.2 | Provide all materials and carry out hydraulic mulch Grass seeding to slopes as specified on the drawings, all to Engineer's approval. | m2 | 2000
X990.3 | Supply and plant approved grass on slopes and maintain until it takes root to the satisfaction of the Engineer. Rate to include for excavation of cut-off drains to divert run-off water from pipe trench alignment. | m2 | 6000
X991 | HEADWALLS, CASCADES AND OUTFALL CHAMBERS
Details as per Dwg No. M430/SD/03-04 (Provisional Quantities)
X991.1 | Excavation
The rates shall include for all strutting, shuttering, stabilising the excavation and preparation of excavated surfaces to receive permanent work.
Excavate for foundations, part backfill after construction and remainder, cart away to tips or use as fill on site, all as directed by the Engineer. Tips to be identified by the Contractor in liaison with the Local Authority.
X991.1.1 | Maximum depth n.e. 1.0m | m3 | 50
X991.1.2 | -Ditto - depth 1.0 to 1.5m | m3 | 85
X991.1.3 | -Ditto - depth exceeding 1.5m | m3 | 35
X991.1.4 | E.O. excavation items for excavation in rock Class 'A' (Provisional) | m3 | 2
X991.1.5 | -Ditto - for excavation in rock Class 'B' (Provisional) | m3 | 25
X991.1.6 | -Ditto - for excavation in rock Class 'C' (Provisional) | m3 | 15
X991.2 | Concrete Works
Provide, mix and place concrete as directed
X991.2.1 | Plain concrete Class 15/20 in 50mm blinding layer under bases/treads. | m2 | 140
PAGE TOTAL CARRIED TO BILL COLLECTION SHEET
X991.2.2 | Vibrated, Reinforced Concrete Class 25/20 in:-
X991.2.2.1 | Footings | m3 | 3
X991.2.2.2 | Bases | m3 | 20
X991.2.2.3 | Walls | m3 | 20
X991.2.2.4 | Treads | m3 | 2
X991.2.2.5 | Risers | m3 | 5
X991.2.2.6 | Roof Slabs | m3 | 10
X991.3 | Reinforcement
Provide and fix high tensile steel reinforcement to SRN 127 including cutting, bending, propping, with spacers and tying as specified.
X991.3.1 | All diameters | kg | 7800
X991.4 | Formwork
Provide and fix shuttering including propping, strutting and striking all as specified.
(i) Vertical Formwork - Class F1 Finish
X991.4.1 | Sides of 200mm treads/ bases/ risers | m | 285
X991.4.2 | Sides of footings - width n.e. 0.2m | m | 20
X991.4.3 | Sides of footings - width exceeding 0.2m | m² | 10
X991.4.4 | External faces of chamber walls/ headwalls - width exceeding 0.2m | m² | 200
(ii) Vertical Formwork - Class F2 Finish
X991.4.5 | Sides of 200mm roof slabs and walls | m | 140
X991.4.6 | Internal faces of chamber walls/ headwalls etc | m² | 160
(iii) Horizontal Formwork - Class F2 Finish
X991.4.7 | Soffites of roof slabs and walls | m² | 25
X991.5 | Walling
Natural Stone Block Walling, Medium Chisel Dressed, Reinforced with 20 swg Hoop Iron at Every Alternate Course, and Bedded, Jointed and Pointed in Cement Mortar (1:4):-
X991.5.1 | 200 mm Walling | m2 | 50
X991.6 | Plastering
12.5mm Thick Gauged Cement Plaster as per specifications on:
X991.6.1 | Natural stone block walling and other surfaces | m2 | 100
X991.7 | Miscellaneous Works
X991.7.1 | Provide for and fix plastic coated step irons in rising outfall chambers for Washouts as specified by the Engineer. Details of chamber are in Dwg Nr. M430/SD/03 | Nr | 60
X991.7.2 | Provide Precast Reinforced Concrete Covers size 600 x 600 x 50mm thick to the rising outlet Chambers. | Nr | 8
PAGE TOTAL CARRIED TO BILL COLLECTION SHEET
X991.8 | Method Related Charges
X991.8.1 | Allow for River diversion, for construction of W.O outfall structure including construction of cofferdam etc., for river crossing works and reinstate after construction. The River / Waterway to be kept operational during construction. The Bidder to submit method statement with Bid for execution of these works. | Item | L.S
X991.8.2 | Method related charges for keeping excavation free of water which may occur through ground water seepage, rain or other means. | Item | L.S
X991.8.3 | Allow for any other method related charges the Bidder feels may be required. These should be indicated below with pricing of each item.
| i) | Item | L.S
| ii) | Item | L.S
X992 | AERIAL CROSSINGS ON PIERS - 3Nr. Crossings
Details as per Dwg Nos. M430/SD/13
Pipe Nominal Bore n.e 900 - 1800mm
X992.1 | Excavation
The rates shall include for all strutting, shuttering, stabilising the excavation faces and preparation of excavated surfaces to receive permanent work.
Excavate for pier footings and Under-River Crossings, part backfill after construction and remainder, cart away to approved tips or use as fill on site, all as directed by the Engineer. Tips to be identified by the Contractor in liaison with the Local Authority.
X992.1.1 | Maximum depth n.e. 1.5m | m3 | 150
X992.1.2 | -Ditto - depth 1.5 to 2.0m | m3 | 50
X992.1.3 | -Ditto - depth exceeding 2.0m | m3 | 90
X992.1.4 | E.O. excavation items for excavation in rock Class 'A' (Provisional) - Blasting not permitted | m3 | 50
X992.1.5 | -Ditto - for excavation in rock Class 'B' (Provisional) - Blasting not permitted | m3 | 70
X992.1.6 | -Ditto - for excavation in rock Class 'C' (Provisional) - Blasting not permitted | m3 | 105
X992.2 | Concrete Works
Provide, mix and place concrete as directed
X992.2.1 | Plain concrete Class 15/20 in 75mm blinding layer under pier footings. | m2 | 30
X992.2.2 | -Ditto- but 75mm thick, on exposed surface of gabions | m2 | 30
X992.2.3 | Vibrated, Reinforced Concrete Class 25/20 in:-
X992.2.3.1 | Footings | m3 | 16
X992.2.3.2 | Piers | m3 | 95
PAGE TOTAL CARRIED TO BILL COLLECTION SHEET
X992.3 | Reinforcement
Provide and fix high tensile steel reinforcement to SRN 127 including cutting, bending, propping, with spacers and tying as specified.
X992.3.1 | 12mm and under | kg | 6100
X992.3.2 | 16mm and over | kg | 9200
X992.4 | Formwork
Provide and fix shuttering including propping, strutting and striking all as specified.
(i) Vertical Formwork - Class F1 Finish
X992.4.1 | Sides of 500mm footings | m2 | 12
X992.4.2 | Sides of piers in foundations | m2 | 160
(ii) Vertical Formwork - Class F2 Finish
X992.4.3 | Outer faces of column piers - width 1.0m - 3.0m | m2 | 185
(iii) Sloping Formwork - Class F2 Finish
X992.4.4 | Sloping face of column head | m2 | 150
X992.5 | Pipe Support Details
Provide all materials, fabricate and install 75mm wide x 15mm thick flat GMS Strap on pipes on piers at Aerial Crossings; Rate to include for supply and installation of Rag Bolts, Rubberoid layers, etc. all as detailed in Drg. No. M430/SD/13; to Engineer's approval.
X992.5.1 | DN 1000 | Nr | 12
X992.6 | Method Related Charges (Applicable to all River Crossings)
X992.6.1 | Allow for River Diversion Works, including construction of cofferdams etc., for river crossing works and reinstate after construction. The Rivers / Waterways to be kept operational during construction. Bidder to submit method statement with Bid for execution of these works. | Item | L.S
X992.6.2 | Method related charges for keeping excavations free of water which may occur through ground water seepage, rain or other means. | Item | L.S
X992.6.3 | Allow for any other method related charges the Bidder feels may be required. These should be indicated below with pricing of each item.
| i) | Item | L.S
| ii) | Item | L.S
PAGE TOTAL CARRIED TO BILL COLLECTION SHEET
X993 | Transverse R.C. Supports to Pipeline on Steep Cross-fall within the Mwache forest (600m Section). 152Nr. R.C. Piers @8m c/c
Details as per Dwg Nos. M430/SD/13
Pipe Nominal Bore n.e 900 - 1800mm
X993.1 | Excavation
The rates shall include for all strutting, shuttering, stabilising the excavation faces and preparation of excavated surfaces to receive permanent work.
Excavate for pier footings, part backfill after construction and remainder, cart away to approved tips or use as fill on site, all as directed by the Engineer. Tips to be identified by the Contractor in liaison with the Local Authority.
X993.1.1 | Maximum depth n.e. 1.5m | m3 | 2150
X993.1.2 | -Ditto - depth 1.5 to 2.0m | m3 | 720
X993.1.3 | -Ditto - depth exceeding 2.0m | m3 | 2500
X993.1.4 | E.O. excavation items for excavation in rock Class 'A' (Provisional) - Blasting not permitted | m3 | 145
X993.1.5 | -Ditto - for excavation in rock Class 'B' (Provisional) - Blasting not permitted | m3 | 1920
X993.1.6 | -Ditto - for excavation in rock Class 'C' (Provisional) - Blasting not permitted | m3 | 510
X993.2 | Concrete Works
Provide, mix and place concrete as directed
X993.2.1 | Plain concrete Class 15/20 in 75mm blinding layer under pier footings. | m2 | 1360
X993.2.3 | Vibrated, Reinforced Concrete Class 25/20 in:-
X993.2.3.1 | Footings | m3 | 680
X993.2.3.2 | Piers | m3 | 840
X993.3 | Reinforcement
Provide and fix high tensile steel reinforcement to SRN 127 including cutting, bending, propping, with spacers and tying as specified.
X993.3.1 | 12mm and under | kg | 80000
X993.3.2 | 16mm and over | kg | 120000
X993.4 | Formwork
Provide and fix shuttering including propping, strutting and striking all as specified.
(i) Vertical Formwork - Class F1 Finish
X993.4.1 | Sides of 500mm footings | m2 | 525
X993.4.2 | Sides of piers in foundations | m2 | 3040
(ii) Vertical Formwork - Class F2 Finish
X993.4.3 | Outer faces of column piers - width 1.0m - 3.0m | m2 | 275
PAGE TOTAL CARRIED TO BILL COLLECTION SHEET
(iii) Sloping Formwork - Class F2 Finish
X993.4.4 | Sloping face of column head | m2 | 2050
X993.5 | Pipe Support Details
Provide all materials, fabricate and install 75mm wide x 15mm thick flat GMS Strap on pipes on piers at Aerial Crossings; Rate to include for supply and installation of Rag Bolts, Rubberoid layers, etc. all as detailed in Drg. No. M430/SD/13; to Engineer's approval.
X993.5.1 | DN 1000 | Nr | 48
X993.6 | Method Related Charges for Construction of Transverse Supports on Steep Cross-fall Section
X993.6.1 | Method related charges for keeping excavations free of water which may occur through ground water seepage, rain or other means. | Item | L.S
X993.6.2 | Allow for provision of mechanized access and working within the Steep Section of the Cross-fall. | Item | L.S
X993.6.3 | Allow for any other method related charges the Bidder feels may be required. These should be indicated below with pricing of each item.
| i) | Item | L.S
| ii) | Item | L.S
X994 | Miscellaneous Works (Provisional)
X994.1 | Allow a Provisional Sum for other Miscellaneous Works that may be required on site to be carried out as directed by the Engineer. | Item | P.S | 10000000 | 10000000
X995 | CATHODIC PROTECTION FOR STEEL PIPES AND FITTINGS:
NOTE: THIS ITEM SHOULD ONLY BE PRICED IF THE BIDDER HAS QUOTED FOR STEEL PIPES AND FITTINGS. BIDDERS QUOTING FOR DUCTILE IRON PIPES AND FITTINGS SHOULD NOT PRICE FOR THESE ITEMS.
X995.1 | Carry out Detailed Design of Cathodic Protection system for the Mwache Twin Trunk Main, total length of pipeline 3.05km. Rate to include for all requisite confirmatory field tests and analysis such as soil resistivity, current drain, natural potential survey, etc., system design and approval.Design to be based on impressed current Cathodic Protection system. | Item | L.S
X995.2 | Supply of all required materials, Installation, Testing and commissioning of the Impressed Current Cathodic Protection system on Steel Mwache Twin Trunk Main as per approved design, total length of pipeline not exceeding 3.05km. | Item | L.S
X995.3 | Bi-monthly assistance by the Specialized Sub-Contractor to verify the performance of the Cathodic Protection System, to carry out the appropriate maintenance if needed and to train MOWASSCO staff on these issues, during the Defects Liability Period. | Item | 6
PAGE TOTAL CARRIED TO BILL COLLECTION SHEET
X996 | WRAPPING OF STEEL FITTINGS AND JOINTS
NOTE: THIS ITEM SHOULD ONLY BE PRICED IF THE BIDDER HAS QUOTED FOR STEEL PIPES AND FITTINGS. BIDDERS QUOTING FOR DUCTILE IRON PIPES AND FITTINGS SHOULD NOT PRICE FOR THESE ITEMS.
X996.1 | Provide all materials and wrap all Steel Fittings with approved Petrolatum Tape such as Denso Tape or appoved equivalent, including an outwrap applied with atleast 55% overlap. Wrapping to be applied on all Steel Fittings without 3LPE coating, including Bends, Tees, Short Pieces, Tapers, couplings and Sockets, etc. Application to be carried out as per Manufacture's Specifications, to the Engineer's Approval | m2 | 500
PAGE TOTAL CARRIED TO BILL COLLECTION SHEET
Note on G151: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Assume all the Washouts will need the bends

## Collection Sheet L1 Bill 2.2
IMPROVEMENT OF DRINKING WATER AND SANITATION SYSTEMS IN MOMBASA: MWACHE CKE 1103
LOT 1: CONSTRUCTION OF THE MWACHE TWIN TRUNK MAIN (TM1), SOUTH MAINLAND TRANSMISSION PIPELINE AND DONGO KUNDU RESERVOIR
BID No. CWWDA/AFD/PQ/W4/2022-2023
BILL No. 2.2 - TWIN TRUNK MAIN SECTION 1 (LINE TM1)
PIPELINE CONSTRUCTION
Amount
(Kshs.)
Page Total, Page 1 of 17
Page Total, Page 2 of 17
Page Total, Page 3 of 17
Page Total, Page 4 of 17
Page Total, Page 5 of 17
Page Total, Page 6 of 17
Page Total, Page 7 of 17
Page Total, Page 8 of 17
Page Total, Page 9 of 17
Page Total, Page 10 of 17
Page Total, Page 11 of 17
Page Total, Page 12 of 17
Page Total, Page 13 of 17
Page Total, Page 14 of 17
Page Total, Page 15 of 17
Page Total, Page 16 of 17
Page Total, Page 17 of 17
Bill No. 2.2 Total Exclusive of VAT carried to Summary Sheet |  | 0

## Lot 1 Bill 3 Instructions
IMPROVEMENT OF DRINKING WATER AND SANITATION SYSTEMS IN MOMBASA: MWACHE CKE 1103
LOT 1; CONSTRUCTION OF THE MWACHE TWIN TRUNK MAIN (TM1), SOUTH MAINLAND TRANSMISSION PIPELINE AND DONGO KUNDU RESERVOIR
BID No. CWWDA/AFD/PQ/W4/2022-2023
BILL No. 3 - SOUTH MAINLAND WATER TRANSMISSION PIPELINE (LINE SM)
INSTRUCTIONS TO BIDDERS
IMPORTANT:
THE BIDDER TO QUOTE FOR ANY ONE OF THE FOLLOWING OPTIONS FOR PIPES AND FITTINGS MATERIALS AND JOINTING. THE SELECTED OPTION TO BE TICKED IN THE SPACE PROVIDED.
OPTION | DESCRIPTION | INDICATE SELECTED OPTION BY TICKING ONE BOX BELOW
OPTION 1 | Ductile Iron Socket and Spigot Pipes and Fittings with Standard Push-On Joints as specified
OPTION 2 | Steel Pipes and Fittings with provision for Field Butt Welded Joints as specified.
ONLY ONE OPTION SHOULD BE SELECTED (TICK ONLY ONE BOX) IF NONE OR BOTH BOXES ARE TICKED, THE BID WILL BE CONSIDERED UNRESPONSIVE AND REJECTED

## Lot 1-Bill 3.1
IMPROVEMENT OF DRINKING WATER AND SANITATION SYSTEMS IN MOMBASA: MWACHE CKE 1103
LOT 1: CONSTRUCTION OF THE MWACHE TWIN TRUNK MAIN (TM1), SOUTH MAINLAND TRANSMISSION PIPELINE AND DONGO KUNDU RESERVOIR
BID No. CWWDA/AFD/PQ/W4/2022-2023
BILL No. 3.1 - SOUTH MAINLAND WATER TRANSMISSION PIPELINE (LINE SM)
SUPPLY OF PIPES, FITTINGS, VALVES AND ANCILLARIES
ITEM No. | DESCRIPTION | UNIT | QUANTITY | RATE (Kshs) | AMOUNT (Kshs)
NOTES:
1. | THIS BILL ONLY COVERS RATES FOR PROCUREMENT OF PIPES AND FITTINGS, TRANSPORT TO CONTRACTOR'S SITE STORE AND STORAGE. INCLUDING SUPPLY OF JOINTING MATERIALS, BOLTS, NUTS, GASKETS, ETC.
2. | RATES FOR TRANSPORT FROM SITE STORE AND INSTALLATION TO BE INCLUDED IN BILL No. 3.2.
3. | BIDDER TO PRICE EITHER FOR STEEL PIPES AND FITTINGS WITH PROVISION FOR FIELD BUTT-WELDED JOINTS AS SPECIFIED OR DUCTILE IRON SOCKET AND SPIGOT PIPES AND FITTINGS WITH STANDARD PUSH-ON JOINTS AS SPECIFIED
4. | ALL RATES TO BE INCLUSIVE OF RELEVANT GOVERNMENT OF KENYA DUTIES AND TAXES, EXCEPT VALUE ADDED TAX (VAT) WHICH IS TO BE ADDED SEPARATELY IN THE GRAND SUMMARY.
5. | ALL PIPES AND FITTINGS TO PRESSURE RATING AS INDICATED FOR EACH ITEM UNLESS OTHERWISE STATED
6. | FOR STEEL PIPELINES, STEEL GRADE AND THICKNESS AS SPECIFIED
7. | PIPELINE EXTERNAL COATING AND INTERNAL LINING AS SPECIFIED FOR THE SELECTED PIPELINE MATERIAL
8. | BIDDERS QUOTING FOR DUCTILE IRON PIPES AND FITTINGS TO PRICE FOR SERIES X ITEMS : OTHER PRICES FOR DUCTILE IRON PIPES AND FITTINGS
9. | IN VIEW OF THE LARGE PIPE DIAMETERS INVOLVED, BIDDERS TO ALLOW FOR REINFORCEMENT OF FITTINGS AS MAYBE REQUIRED, ALL AS PER THE AWWA MANUAL OF WATER SUPPLY PRACTICES (AWWA M11); REINFORCEMENT OF PIPE FITTINGS EITHER BY COLLAR PLATE, WRAPPER PLATE OR BY CROTCH-PLATE, AS MAY BE REQUIRED. BIDDER TO INCLUDE RATE FOR REINFORCEMENT OF FITTINGS IN THEIR RATES FOR RESPECTIVE FITTINGS
CLASS I: PIPE WORK - PIPES
I4 | Ductile Iron Pipes or Steel Pipes; Joints as specified
| Ductile Iron Socket and Spigot Pipes with Standard Push-On Joints (class 25, cement mortar lining, zinc-aluminium coating) OR Steel Pipes with provision for Field Butt-Welded Joints (minimum yield strength 290 Mpa, epoxy lining, 3-layer polyethylene coating) | [9 empty] | 110 | ISD
144 | DN 900 mm; Minimum Wall Thickness 8mm | m | 6400 | [6 empty] | ASP | 415 | 41085
I45 | DN 1000 mm; Minimum Wall Thickness 8.8mm | m | 22750 | [7 empty] | 477.5 | 47272.5
I5 | High Density Polyethylene Pipes (HDPE)
Butt-fusion weld jointed HDPE Pipes - PN 16
I51 | Nominal Bore 110 mm (provisional length) | m | 1800
PAGE TOTAL CARRIED TO BILL COLLECTION SHEET
I52 | Nominal Bore 225 mm (provisional length) for Washout Drainage | m | 2000
CLASS J: PIPE WORK - FITTINGS AND VALVES
J3 | Ductile Iron Fittings or Steel Fittings; Joints as specified
J31 | Bends
J311 | Nominal Bore 200mm; Ductile Iron Socket and Spigot or Double Socketed Bends OR Steel Socket and Spigot Bends
J311.1 | 90⁰ DN 200, PN 16 (provisional) | Nr | 45
J312.1 | Nominal bore 250mm; Double Flanged Bend
J312.1.1 | 45⁰ DN 250, PN 16 | Nr | 5
J313 | Nominal Bore 500mm; Ductile Iron Double flanged Bends OR Steel Double flanged Bends
J313.1 | 45⁰ DN 500, PN 16 (provisional) | Nr | 2 |  |  | 9367.785 | 6245.19 | LOT 1 BILL 2 | 1.5
J313.2 | 90⁰ DN 500, PN 16 (provisional) | Nr | 2 |  |  | 9367.785 | 6245.19 | LOT 1 BILL 2 | 1.5
J314.1 | Nominal bore 800mm; Double Flanged Bend
J314.1.1 | 45⁰ DN 800, PN 16 | Nr | 5
J314.2 | Nominal Bore 900mm; Double Flanged Bend
J314.2.1 | 45⁰ DN 900, PN 16 | Nr | 5
J314.3 | Nominal Bore 900mm; Ductile Iron Socket and Spigot or Double Socketed Bends with Standard Push-On Joints OR Steel plain ended Bends with provision for field butt-welded Joints
J314.3.1 | 11.25⁰ DN 900, PN 16 | Nr | 13
J314.3.2 | 22.5⁰ DN 900, PN 16 | Nr | 2
J314.3.3 | 90⁰ DN 900, PN 16 | Nr | 2
J315.2 | Nominal Bore 1000mm; Ductile Iron Socket and Spigot or Double Socketed Bends with Standard Push-On Joints OR Steel plain ended Bends with provision for field butt-welded Joints
J315.2.1 | 11.25⁰ DN 1000, PN 16 | Nr | 143
J315.2.2 | 22.5⁰ DN 1000, PN 16 | Nr | 40
J315.2.4 | 45⁰ DN 1000, PN 16 | Nr | 6
J32 | Junctions and Branches
All Flanged Tee
J321.1 | DN 200 x DN 200, PN 16 all Flanged Tee | Nr | 1
J323.1 | DN 500 x DN 500, PN 16 all Flanged Tee for Non Return Valves | Nr | 1 |  |  | 9367.785 | 6245.19 | LOT 1 BILL 2 | 1.5
J324.1 | DN 900 x DN 800, PN 16 all Flanged Tee for Air Valves | Nr | 6
J325.1 | DN 1000 x DN 200, PN 16 all Flanged Tee for Air Valves within Line Valve Chambers | Nr | 7
J325.2 | DN 1000 x DN 250, PN 16 all Flanged Tee for Interconnection | Nr | 1
J325.3 | DN 1000 x DN 500, PN 16 all Flanged Tee for Air Valves | Nr | 1 |  |  | 0 | 581605.53 | LOT 1 BILL 2 | 0
J325.4 | DN 1000 x DN 800, PN 16 all Flanged Tee Tee for Air Valves | Nr | 40
All Flanged Level Invert Tee
J324.2 | DN 900 x DN 200, PN 16 all Flanged Tee for Washouts | Nr | 5
PAGE TOTAL CARRIED TO BILL COLLECTION SHEET
J325.5 | DN 1000 x DN 200, PN 16 all Flanged Tee for Washouts | Nr | 41
J33 | Tapers
All Flanged Concentric Taper
J332.1 | DN 250 x DN 200, PN 16 | Nr | 1
J334.1 | DN 900 x DN 800, PN 16 | Nr | 3
J335.1 | DN 1000 x DN 900, PN 16 | Nr | 4
J34 | Ferrous Couplings
J341.1 | DN 200, PN 16 - Straight Coupling | Nr | 2
J341.2 | DN 200, PN 16 - Stepped Coupling | Nr | 45
J342.1 | DN 250, PN 16 - Straight Coupling | Nr | 2
J343.1 | DN 500, PN 16 - Straight Coupling | Nr | 4 |  |  | 0 | 82115.55 | LOT 1 BILL 2 | 0
J344.1 | DN 900, PN 16 - Straight Coupling (Provisional) | Nr | 3
J345.1 | DN 1000, PN 16- Straight Coupling (Provisional) | Nr | 12
J35 | Ferrous Flange Adaptor
J351.1 | DN 200, PN 16 | Nr | 42
J352.1 | DN 250, PN 16 | Nr | 4
J353.1 | DN 500, PN 16 | Nr | 3 |  |  | 0 | 207978.53 | LOT 1 BILL 2 | 0
J38 | Straight Specials
Plain Ended Pipes with Puddle Flanges (location of Puddle Flange as specified in Drawings)
J381.1 | DN 200, PN 16, 1.2m long (Provisional) | Nr | 5
J383.1 | DN 500, PN 16, 6m long (cut to suit on site) | Nr | 1 |  |  | 0 | 431960.38 | LOT 1 BILL 2, using PN 25 5.0m Long | 0
J384.1 | DN 900 PN 16, 1.5m long with puddle flange (Provisional) | Nr | 2
Plain Ended Pipes without Puddle Flanges
J381.2 | DN 200, PN 16, 1.2m long | Nr | 45
Flanged Spigot Pipes without Puddle Flanges
J381.3 | DN 200, PN 16, 1.2m long | Nr | 2
J382.1 | DN 250, PN 16, 1.2m long | Nr | 3
J382.2 | DN 250, PN 16, 2.5m long | Nr | 2
J383.2 | DN 500, PN 16, 1.2m long | Nr | 2 |  |  | 0 | 431960.38 | LOT 1 BILL 2, using PN 25 5.0m Long | 0
J383.3 | DN 500, PN 16, 6m long (cut to suit on site) | Nr | 1 |  |  | 0 | 431960.38 | LOT 1 BILL 2, using PN 25 5.0m Long | 0
J384.2 | DN 900, PN 16, 1.5m long | Nr | 13
J385.1 | DN 1000, PN 16, 1.5m long | Nr | 92
J385.2 | DN 1000, PN 16, 3m long | Nr | 30
Flanged Spigot Pipes with Puddle Flanges (location of Puddle Flange as specified in Drawings)
J382.3 | DN 250, PN 16, 1.2m long with puddle flange | Nr | 3
J382.4 | DN 250, PN 16, 2.5m long with puddle flange | Nr | 2
J382.5 | DN 250, PN 16, 1.25m long with puddle flange | Nr | 2
J383.4 | DN 500, PN 16, 1.2m long with puddle flange | Nr | 4 |  |  | 0 | 431960.38 | LOT 1 BILL 2, using PN 25 5.0m Long | 0
J384.3 | DN 900, PN 16, 1.5m long with puddle flange | Nr | 12
J385.3 | DN 1000, PN 16, 1.5m long with puddle flange | Nr | 91
PAGE TOTAL CARRIED TO BILL COLLECTION SHEET
Double Flanged Pipes without Puddle Flanges
J382.6 | DN 250, PN 16, 1.25m long (Provisional) | Nr | 2
J385.4 | DN 1000, PN 16, 1.5m long | Nr | 2
J385.5 | DN 1000, PN 16, 3m long | Nr | 25
J385.6 | DN 1000, PN 16, 4m long | Nr | 87
J385.7 | DN 1000, PN 16, 5m long | Nr | 59
J385.8 | DN 1000, PN 16, 6m long | Nr | 22
J385.9 | DN 1000, PN 16, 8m long | Nr | 78
J385.10 | DN 1000, PN 16, 10m long | Nr | 57
Double Flanged Pipes with puddle flanges (location of Puddle Flange as specified in Drawings)
J383.5 | DN 500, PN 16, 1.2m long | Nr | 2 |  |  | 0 | 431960.38 | LOT 1 BILL 2, using PN 25 5.0m Long | 0
J383.6 | DN 500, PN 16, 2.5m long | Nr | 1 |  |  | 0 | 431960.38 | LOT 1 BILL 2, using PN 25 5.0m Long | 0
J383.7 | DN 500, PN 16, 5m long | Nr | 1 |  |  | 0 | 235560.3204 | LOT 1 BILL 2 | 0
J384.4 | DN 800, PN 16, 4m long with puddle flange | Nr | 2
J384.5 | DN 800, PN 16, 8m long with puddle flange | Nr | 2
J384.6 | DN 900, PN 16, 4.5m long with puddle flange | Nr | 2
J384.7 | DN 900, PN 16, 9m long with puddle flange | Nr | 2
J385.11 | DN 1000, PN 16, 1.5m long with puddle flange | Nr | 2
Special Fittings
J381.4 | DN 200, PN 16, special double flanged pipe 325mm long with flange to suit 800mm dia. tee on one end and 200mm dia flange on the other end as per Dwg No. M430/SD/02 (Detail 1). | Nr | 50
J384.8 | DN 800 PN 16 Dismantling Joint (Viking Johnson dismantling joint, nominal length 300mm or approved equivalent) | Nr | 3
J384.9 | DN 900 PN 16 Dismantling Joint (Viking Johnson dismantling joint, nominal length 307mm or approved equivalent) | Nr | 3
J385.12 | DN 1000 PN 16 Dismantling Joint (Viking Johnson dismantling joint, nominal length 307mm or approved equivalent) | Nr | 6
J8 | Valves and Penstocks
J81 | Flanged Gate Valve
J811.1 | DN 200, PN 16, with handwheel (Isolating Valve for Air Valves) | Nr | 51
J811.2 | DN 200, PN 16, with Extension Spindle, length n.e. 5.0m without handwheel (for washouts) | Nr | 45
J812.1 | DN 250, PN 16, with handwheel (for Interconnection) | Nr | 1
J813.1 | DN 500, PN 16, with handwheel (for Interconnection) | Nr | 2 |  |  | 0 | 86625 | LOT 1 BILL 2 | 0
J83 | Flanged Non Return Valve
J832.1 | DN 250, PN 16 | Nr | 1
J833.1 | DN 500, PN 16 | Nr | 2 |  |  | 0 | 86625 | LOT 1 BILL 2 | 0
J84 | Flanged Butterfly Valve complete with Gear Mechanism designed to slow down flow reduction at end of closure as specified and Hand Wheel as specified
J844.1 | DN 900, PN 16 | Nr | 2
J845.1 | DN 1000, PN 16 | Nr | 7
PAGE TOTAL CARRIED TO BILL COLLECTION SHEET
J86 | Air Valve
J861 | Flanged Double Action Non-Slam (Anti-Surge) Air Valve (DAV) as specified
J861.1 | DN 200, PN 16 | Nr | 51
J87 | Flanged Flow Control Valve
J873 | DN 500, PN 16 | Nr | 1
J9 | Electromagnetic Water Meters
J992.1 | DN 250 All Flanged Battery Powered Electromagnetic Water Meter to PN 16, complete with accessories; Minimum Battery Life 6 Years. | Nr | 1
J993.1 | DN 500 All Flanged Battery Powered Electromagnetic Water Meter to PN 16 complete with accessories; Minimum Battery Life 6 Years. | Nr | 1 |  |  |  |  | 0
J994.1 | DN 800 All Flanged Battery Powered Electromagnetic Water Meter to PN 16 complete with accessories; Minimum Battery Life 6 Years. | Nr | 2
J994.2 | DN 900 All Flanged Battery Powered Electromagnetic Water Meter to PN 16 complete with accessories; Minimum Battery Life 6 Years. | Nr | 1
CLASS X: OTHER COSTS FOR DUCTILE IRON PIPES & FITTINGS
Note: This item is only to be priced if the Bidder has quoted for Ductile Iron Pipes & Fittings. Bidders quoting for Steel Pipes and Fittings should not price this item.
X990 | Additional protection for Ductile Iron Pipes and Fittings in areas of high corrosivity
X990.1 | Carry out Field Tests and Analysis to confirm the specified external coating of Ductile Iron Pipes and Fittings or propose an alternative if required at particular locations | m | 29150
Extra over cost of supply of Pipes and Fittings (Class I and J) for factory heat applied fused polyurethane coating to EN 15189 to Ductile Iron Pipes from CH 6+200 to CH 6+800 (see drawing M430/MP/SM/06)
X990.2 | DN 1000mm | m | 600
Ductile Iron Pipes and Bends with Self-Anchored Joints
X999 | Extra-over cost on top of Items I4 and J31 for the supply of Ductile Iron Pipes and Bends with Self-Anchored Joints
X999.1 | DN 900mm Pipes with Self-Anchored Joints | m | 50
X999.2 | DN 1000mm Pipes with Self-Anchored Joints | m | 200
X999.3 | DN 900mm D.I. Bends with Self-Anchored Joints, assorted angle sizes | Nr. | 5
X999.4 | DN 1000mm D.I. Bends with Self-Anchored Joints, assorted angle sizes | Nr. | 10
PAGE TOTAL CARRIED TO BILL COLLECTION SHEET

## Collection Sheet Bill No. 3.1
IMPROVEMENT OF DRINKING WATER AND SANITATION SYSTEMS IN MOMBASA: MWACHE CKE 1103
LOT 1; CONSTRUCTION OF THE MWACHE TWIN TRUNK MAIN (TM1), SOUTH MAINLAND TRANSMISSION PIPELINE AND DONGO KUNDU RESERVOIR
BID No. CWWDA/AFD/PQ/W4/2022-2023
BILL No. 3.1 - SOUTH MAINLAND WATER TRANSMISSION PIPELINE (LINE SM)
SUPPLY OF PIPES, FITTINGS, VALVES AND ANCILLARIES
Amount
(Kshs.)
Page Total, Page 1 of 5
Page Total, Page 2 of 5
Page Total, Page 3 of 5
Page Total, Page 4 of 5
Page Total, Page 5 of 5
Bill No. 3.1 Total Exclusive of VAT carried to Summary Sheet |  | 0

## Lot 1-Bill 3.2
IMPROVEMENT OF DRINKING WATER AND SANITATION SYSTEMS IN MOMBASA: MWACHE CKE 1103
LOT 1: CONSTRUCTION OF THE MWACHE TWIN TRUNK MAIN (TM1), SOUTH MAINLAND TRANSMISSION PIPELINE AND DONGO KUNDU RESERVOIR
BID No. CWWDA/AFD/PQ/W4/2022-2023
BILL No. 3.2 - SOUTH MAINLAND WATER TRANSMISSION PIPELINE (LINE SM)
PIPELINE CONSTRUCTION
ITEM No. | DESCRIPTION | UNIT | QUANTITY | RATE (Kshs) | AMOUNT (Kshs)
NOTES:
1. | The South Mainland Water Transmission Pipeline is to be laid generally within the same wayleave as the existing Marere and Kaya Bombo Pipelines which are active, with the proposed line crossing to the existing lines at some points. The pipeline alignment traverses through a number of valleys along its entire alignment, notably crossing the 450m wide Mwache Creek and numerous seasonal rivers and streams, both narrow and wide. A section of the pipeline is to be laid within the Mwache forest, characterized by a dense thicket and steep topography. Though the pipeline alignment is within a rural set-up, sections of the line are to be laid within trading centres and along busy murram roads connecting villages and trading centres. Specific conditions in execution of these works are deemed to be included in the Contractor's Rates.The Contractor will be required to submit a Method Statement for execution of works under these specific conditions for approval prior to execution of the works. These include, but are not limited to the following; i) No blasting will be permitted ii) The contractor to maintain uninterrupted continuity of Water Supply in existing Mains iii) Pedestrians and Vehicular access to individual Shops/ Plots, Houses, etc. to be maintained at all times. Where necessary, alternative temporary access to be availed iv) Safety hoarding, lighting, bands, warning signs, etc. to be maintained at all times. v) Immediate Reinstatement and Stabilization of Slopes upon laying of the Pipeline.
2. | The Contractor shall carry out pilot excavations along the pipeline route to establish locations and alignment of existing Telecommunication and Fibre Optic Cables and other buried services, if any, prior to actual trench excavation, all in close liaison with service providers. It shall be deemed that any costs for crossing existing Telecommunication and Fibre Optic Cables is included in the Contractor's Rates. Any claims thereof SHALL NOT be paid and damages caused on the same as a result of execution of the works shall be the Contractor's liability. These will be duly repaired at the Contractor's cost. The Contractor’s rates should allow for any measures necessary to deal with the terrain, provision of access road to work site, liason with the relevant Authorities and local residents, payment of any required statutory charges, etc. The costs for compliance shall be deemed to be covered by the Contractor's Rates.
3. | The proposed works are within the Coastal Region, generally characterized by a corrosive environment and soils. Bidders quoting for Steel Pipes and Fittings shall be required to price for Cathodic Protection of the entire Transmission Pipeline (Item X994). Installation of the Cathodic Protection System to be carried out by a certified approved Specialized Sub-Contractor.
4. | All Rates to include for Government of Kenya Duties and Taxes, Except Value Added Tax (VAT).
5. | Value Added Tax (VAT) to be added separately in the Grand Summary.
PAGE TOTAL CARRIED TO BILL COLLECTION SHEET
CLASS A: GENERAL ITEM
A260 | Testing of Works
Pipeline Testing and Commissioning, including provision of all Equipment, Materials and works necessary for Testing, such as but not limited to thrust blocks, anchor blocks, provision, transportation and use of water, requisite pipe fittings, etc., successful testing to specified pressure and safe disposal of used water.
NOTE: Any additional fittings that may be neccecitated by the Contractor's Methodology for testing shall be supplied and installed at the Contractor's own cost.
A260.1.1 | DN 900mm | m | 6400
A260.1.2 | DN 1000mm | m | 22750
Disinfection of Pipe lines: Flushing with clear water, filling with water containing 0.05 g/l calcium hypochlorite, left for 24 hours. This includes supply of all necessary equipment, materials, chemicals and water, measurement of residual chlorine, all as specified and safe disposal of disinfecting water to Engineer's approval.
A260.2.1 | DN 900 Pipeline | m | 6400
A260.2.2 | DN 1000 Pipeline | m | 22750
A3 | Method Related Charges
A35 | Temporary Works
A35.1 | Working within available limited wayleave, include costs for double / multiple handling of excavated materials if required, as well as provision of alternative access to private property during execution of the works. | Item | L.S
A35.2 | Working within marshy areas with weak soil formation and/or within permanently flooded sections of the Mwache Creek, with weak soil formations, include for construction of cofferdams, dewatering of excavation areas and keeping them free of water during execution of the works. Contractor to provide a Method Statement for carrying out the works | Item | L.S
A35.3 | Keeping trenches free of excessive groundwater, seepage or water from whatever source | Item | L.S
A35.4 | Allow Provisional Sum for Liaison, facilitation with local residents and payment for accesses | Item | P.S | 3000000 | 3000000
A35.5 | Allow for carrying out Pilot Excavation, exposing and identification of existing UNDERGROUND SERVICES (water lines, sewerlines, storm water drains, telephone/electricity ducts, fibre optic cables, etc.) prior to setting out and excavation of the pipeline. Pilot excavation n.e. 3m depth on approx 5m wide corridor, estimate No. of pilot holes along the Pipeline route is 300Nr. | Item | L.S
A35.6 | Allow for crossing existing UNDERGROUND SERVICES (water lines, sewerlines, storm water drains, telephone/electricity ducts, fibre optic cables (including cables for security cameras), etc.), including reinstatement to original states and liason with the relevant body for the inspection/ approval during execution of the works. Nominal bore up to - 1800mm | Item | L.S
PAGE TOTAL CARRIED TO BILL COLLECTION SHEET
A35.7 | Allow a Provisional Sum for re-alignment of existing services, both buried and above ground, as may be required and directed on site, to create space for laying of proposed Transmission Mains. This item covers re-alignment/re-routing of existing water mains, Telecommunication cables, buried and overhead power lines where appropriate. | Item | P.S | 2500000 | 2500000
A35.8 | Allow for any other method related charges the Bidder feels may be required. These should be indicated below with pricing of each item (Bidder may attach additional sheets if necessary):
| i) | Item | L.S
| ii) | Item | L.S
CLASS D: DEMOLITION AND SITE CLEARANCE
D110 | General site clearance along easement (including top soil removal, limited to the trench width) | ha | 17
D2 | Tree Cutting
Cut down trees, grub up roots and cart away to tips
D210.1 | Girth: 0.5 m - 1.0 m | Nr | 50
D210.2 | Girth: 1.0 m - 2 m | Nr | 120
D220.1 | Girth 2.0 m - 3 m | Nr | 200
D220.2 | Girth 3.0 m - 5 m | Nr | 60
D310 | Remove stump dia. 0.5 - 1m | Nr | 30
D320 | Remove stump dia. exceeding 1m | Nr | 30
CLASS E: EARTHWORKS
E220 | Mass Excavation in selected areas to level localized high points and to remove imported deposited material on pipeline alignment to original ground level as directed by the Engineer prior to excavation of pipeline trenches. Include for transportation and disposal of excavated material to approved tips identified by the Contractor in liaison with Local Authorities. | m³ | 45000
CLASS I: PIPE WORK - PIPES
Transport from Site Store, Lay and Joint Pipes in Trenches, include for excavation, preparation of Surfaces, Disposal of Excavated Material, Shoring Sides of Excavation and Backfilling
Note: Trench width and minimum cover to pipes is as per the Specification. The cost shall include for strutting, shuttering, stabilizing the earth faces of trenches and keeping the trenches free of water from whatever source by pumping or other means and cost of use of selected soil from the excavated material for compaction in bed and surround to backfilling of trenches, etc., all as specified.
PAGE TOTAL CARRIED TO BILL COLLECTION SHEET
I4 | Ductile Iron Pipes OR Steel Pipes; Joints as specified
Ductile Iron Socket and Spigot Pipes with Standard Push-On Joints OR Steel Pipes with provision for Field Butt-welded Joints. Rate for Welded Steel Pipe to include for provision of all materials and wrapping of all Welded joints as specified
I44 | Nominal Bore 900mm in trenches
I442 | Depth 1.5m - 2.0m | m | 290
I443 | Depth 2.0 m - 2.5 m | m | 1640
I444 | Depth 2.5 m - 3.0 m | m | 2200
I445 | Depth 3.0 m - 3.5 m | m | 1080
I446 | Depth 3.5 m - 5 m | m | 1190
I45 | Nominal Bore 1000mm in trenches
I451 | Nominal Bore 1000mm not in trenches (For aerial crossings) | m | 1500
I452 | Depth not exceeding 1.5 m | m | 470
I453 | Depth 1.5 m - 2.0 m | m | 800
I454 | Depth 2.0 m - 2.5 m | m | 4300
I455 | Depth 2.5 m -3.0 m | m | 6220
I456 | Depth 3.0 m - 3.5 m | m | 4550
I457 | Depth 3.5m - 4.0 m | m | 2750
I458 | Depth exceeding 4.0 m | m | 2160
I5 | High Density Polyethylene Pipes (HDPE)
I51 | Butt-fusion weld jointed HDPE Pipes - PN 16 Nominal Bore 110mm in trenches
I512 | Depth not exceeding 1.5 m | m | 360
I513 | Depth 1.5m - 2.0 m | m | 540
I514 | Depth 2.0 m - 2.5m | m | 900
I52 | Butt-fusion weld jointed HDPE Pipes - PN 16 Nominal Bore 225mm in trenches
I522 | Depth n.e 1.5 | m | 140
I523 | Depth 1.5m - 2.0m | m | 140
I524 | Depth 2.0m - 2.5m | m | 195
I525 | Depth 2.5m - 3.0m | m | 195
I526 | Depth 3.0m - 3.5m | m | 195
I527 | Depth 3.5m - 4m | m | 389
I528 | Depth exceeding 4m, Maximum Depth 6m | m | 746
PAGE TOTAL CARRIED TO BILL COLLECTION SHEET
CLASS J: PIPE WORK - FITTINGS AND VALVES
Transport from Site Store, Lay and Joint Pipe Fittings in Trench/on Aerial Crossings, Include for Excavation, Preparation of Surfaces, Disposal of Excavated Material, Shoring Sides of Excavation and Backfilling. Rate to include for Transport to Site and Installation of all Jointing Materials, Bolts, Nuts, Gaskets, etc.
J3 | Ductile Iron Fittings OR Steel Fittings; Joints as specified
J31 | Bends
J311.1 | Nominal Bore 200mm; Ductile Iron Socket and Spigot or Double Socketed Bends OR Steel Socket and Spigot Bends
J311.1.1 | 90⁰ DN 200, PN 16 (provisional) | Nr | 45
J312.1 | Nominal bore 250mm; Double Flanged Bend
J312.1.1 | 45⁰ DN 250, PN 16 | Nr | 5
J313 | Nominal Bore 500mm; Ductile Iron Double flanged Bends OR Steel Double flanged Bends
J313.1 | 45⁰ DN 500, PN 16 (provisional) | Nr | 2
J313.2 | 90⁰ DN 500, PN 16 (provisional) | Nr | 2
J314.1 | Nominal bore 800mm; Double Flanged Bend
J314.1.1 | 45⁰ DN 800, PN 16 | Nr | 5
J314.2 | Nominal Bore 900mm; Double Flanged Bend
J314.2.1 | 45⁰ DN 900, PN 16 | Nr | 5
J314.3 | Nominal Bore 900mm; Ductile Iron Socket and Spigot or Double Socketed Bends with Standard Push-On Joints OR Steel plain ended Bends with provision for field butt-welded Joints
J314.3.1 | 11.25⁰ DN 900, PN 16 | Nr | 13
J314.3.2 | 22.5⁰ DN 900, PN 16 | Nr | 2
J314.3.3 | 90⁰ DN 900, PN 16 | Nr | 2
J315.2 | Nominal Bore 1000mm; Ductile Iron Socket and Spigot or Double Socketed Bends with Standard Push-On Joints OR Steel plain ended Bends with provision for field butt-welded Joints
J315.2.1 | 11.25⁰ DN 1000, PN 16 | Nr | 143
J315.2.2 | 22.5⁰ DN 1000, PN 16 | Nr | 40
J315.2.4 | 45⁰ DN 1000, PN 16 | Nr | 6
J32 | Junctions and Branches
All Flanged Tee
J321.1 | DN 200 x DN 200, PN 16 all Flanged Tee | Nr | 1
J323.1 | DN 500 x DN 500, PN 16 all Flanged Tee for Non Return Valves | Nr | 1
J324.1 | DN 900 x DN 800, PN 16 all Flanged Tee for Air Valves | Nr | 6
PAGE TOTAL CARRIED TO BILL COLLECTION SHEET
J325.1 | DN 1000 x DN 200, PN 16 all Flanged Tee for Air Valves within Line Valve Chambers | Nr | 7
J325.2 | DN 1000 x DN 250, PN 16 all Flanged Tee for Interconnection | Nr | 1
J325.3 | DN 1000 x DN 500, PN 16 all Flanged Tee for Air Valves | Nr | 1
J325.4 | DN 1000 x DN 800, PN 16 all Flanged Tee Tee for Air Valves | Nr | 40
All Flanged Level Invert Tee
J324.2 | DN 900 x DN 200, PN 16 all Flanged Tee for Washouts | Nr | 5
J325.5 | DN 1000 x DN 200, PN 16 all Flanged Tee for Washouts | Nr | 41
J33 | Tapers
All Flanged Concentric Taper
J332.1 | DN 250 x DN 200, PN 16 | Nr | 1
J334.1 | DN 900 x DN 800, PN 16 | Nr | 3
J335.1 | DN 1000 x DN 900, PN 16 | Nr | 4
J34 | Ferrous Couplings
J341.1 | DN 200, PN 16 - Straight Coupling | Nr | 2
J341.2 | DN 200, PN 16 - Stepped Coupling | Nr | 45
J342.1 | DN 250, PN 16 - Straight Coupling | Nr | 2
J343.1 | DN 500, PN 16 - Straight Coupling | Nr | 4
J344.1 | DN 900, PN 16 - Straight Coupling (Provisional) | Nr | 3
J345.1 | DN 1000, PN 16- Straight Coupling (Provisional) | Nr | 12
J35 | Ferrous Flange Adaptor
J351.1 | DN 200, PN 16 | Nr | 42
J352.1 | DN 250, PN 16 | Nr | 4
J353.1 | DN 500, PN 16 | Nr | 3
J38 | Straight Specials
Plain Ended Pipes with Puddle Flanges (location of Puddle Flange as specified in Drawings)
J381.1 | DN 200, PN 16, 1.2m long (Provisional) | Nr | 5
J383.1 | DN 500, PN 16, 6m long (cut to suit on site) | Nr | 1
J384.1 | DN 900 PN 16, 1.5m long with puddle flange (Provisional) | Nr | 2
Plain Ended Pipes without Puddle Flanges
J381.2 | DN 200, PN 16, 1.2m long | Nr | 45
Flanged Spigot Pipes without Puddle Flanges
J381.3 | DN 200, PN 16, 1.2m long | Nr | 2
J382.1 | DN 250, PN 16, 1.2m long | Nr | 3
J382.2 | DN 250, PN 16, 2.5m long | Nr | 2
PAGE TOTAL CARRIED TO BILL COLLECTION SHEET
J383.2 | DN 500, PN 16, 1.2m long | Nr | 2
J383.3 | DN 500, PN 16, 6m long (cut to suit on site) | Nr | 1
J384.2 | DN 900, PN 16, 1.5m long | Nr | 13
J385.1 | DN 1000, PN 16, 1.5m long | Nr | 92
J385.2 | DN 1000, PN 16, 3m long | Nr | 30
Flanged Spigot Pipes with Puddle Flanges (location of Puddle Flange as specified in Drawings)
J382.3 | DN 250, PN 16, 1.2m long with puddle flange | Nr | 3
J382.4 | DN 250, PN 16, 2.5m long with puddle flange | Nr | 2
J382.5 | DN 250, PN 16, 1.25m long with puddle flange | Nr | 2
J383.4 | DN 500, PN 16, 1.2m long with puddle flange | Nr | 4
J384.3 | DN 900, PN 16, 1.5m long with puddle flange | Nr | 12
J385.4 | DN 1000, PN 16, 1.5m long with puddle flange | Nr | 91
Double Flanged Pipes without Puddle Flanges
J382.6 | DN 250, PN 16, 1.25m long (Provisional) | Nr | 2
J385.5 | DN 1000, PN 16, 1.5m long | Nr | 2
J385.6 | DN 1000, PN 16, 3m long | Nr | 25
J385.7 | DN 1000, PN 16, 4m long | Nr | 87
J385.8 | DN 1000, PN 16, 5m long | Nr | 59
J385.9 | DN 1000, PN 16, 6m long | Nr | 22
J385.10 | DN 1000, PN 16, 8m long | Nr | 78
J385.11 | DN 1000, PN 16, 10m long | Nr | 57
Double Flanged Pipes with puddle flanges (location of Puddle Flange as specified in Drawings)
J383.5 | DN 500, PN 16, 1.2m long | Nr | 2
J383.6 | DN 500, PN 16, 2.5m long | Nr | 1
J383.7 | DN 500, PN 16, 5m long | Nr | 1
J384.4 | DN 800, PN 16, 4m long with puddle flange | Nr | 2
J384.5 | DN 800, PN 16, 8m long with puddle flange | Nr | 2
J384.6 | DN 900, PN 16, 4.5m long with puddle flange | Nr | 2
J384.7 | DN 900, PN 16, 9m long with puddle flange | Nr | 2
J385.11 | DN 1000, PN 16, 1.5m long with puddle flange | Nr | 2
Special Fittings
J381.4 | DN 200, PN 16, special double flanged pipe 325mm long with flange to suit 800mm dia. tee on one end and 200mm dia flange on the other end as per Dwg No. M430/SD/02 (Detail 1). | Nr | 50
PAGE TOTAL CARRIED TO BILL COLLECTION SHEET
J384.8 | DN 800 PN 16 Dismantling Joint (Viking Johnson dismantling joint, nominal length 300mm or approved equivalent) | Nr | 3
J384.9 | DN 900 PN 16 Dismantling Joint (Viking Johnson dismantling joint, nominal length 307mm or approved equivalent) | Nr | 3
J385.12 | DN 1000 PN 16 Dismantling Joint (Viking Johnson dismantling joint, nominal length 307mm or approved equivalent) | Nr | 6
J8 | Valves and Penstocks
J81 | Flanged Gate Valve
J811.1 | DN 200, PN 16, with handwheel (Isolating Valve for Air Valves) | Nr | 51
J811.2 | DN 200, PN 16, with Extension Spindle, length n.e. 5.0m without handwheel (for washouts) | Nr | 45
J812.1 | DN 250, PN 16, with handwheel (for Interconnection) | Nr | 1
J813.1 | DN 500, PN 16, with handwheel (for Interconnection) | Nr | 2
J83 | Flanged Non Return Valve
J832.1 | DN 250, PN 16 | Nr | 1
J833.1 | DN 500, PN 16 | Nr | 2
J84 | Flanged Butterfly Valve complete with Gear Mechanism designed to slow down flow reduction at end of closure as specified and Hand Wheel as specified
J844.1 | DN 900, PN 16 | Nr | 2
J845.1 | DN 1000, PN 16 | Nr | 7
J86 | Air Valve
J861 | Flanged Double Action Non-Slam (Anti-Surge) Air Valve (DAV) as specified
J861.1 | DN 200, PN 16 | Nr | 51
J87 | Flanged Flow Control Valve
J873 | DN 500, PN 16 | Nr | 1
J9 | Electromagnetic Water Meters
J992.1 | DN 250 All Flanged Battery Powered Electromagnetic Water Meter to PN 16, complete with accessories; Minimum Battery Life 6 Years. | Nr | 1
J993.1 | DN 500 All Flanged Battery Powered Electromagnetic Water Meter to PN 16 complete with accessories; Minimum Battery Life 6 Years. | Nr | 1
J994.1 | DN 800 All Flanged Battery Powered Electromagnetic Water Meter to PN 16 complete with accessories; Minimum Battery Life 6 Years. | Nr | 2
J994.2 | DN 900 All Flanged Battery Powered Electromagnetic Water Meter to PN 16 complete with accessories; Minimum Battery Life 6 Years. | Nr | 1
PAGE TOTAL CARRIED TO BILL COLLECTION SHEET
CLASS K: PIPE WORK - CHAMBERS AND PIPE WORK ANCILLARIES
Chambers, ducts, culverts, crossings, thrust and anchor blocks, reinstatement and others pipeworks and ancillaries.
Note:- Items for Work in this class shall include:- - Excavation, dewatering, preparation of surfaces, disposal of excavated material, shoring sides of excavation, backfilling and removal of redundant services. - Concrete, reinforcement, formwork, joints and finishes. - Tips for disposal of excavated material or debris to be identified by the Contractor in liaison with the Local Authorities. - Rate to include for placing and compaction of pipe embedment material below the chamber and filling around pipe before construction of chamber - All Chambers to be fitted with adequate drainage system and permanent ventilation as per details or as directed by Engineer in Site. - Chambers to be fitted with plastic coated step irons or Access ladders as specified; and lockable covers to access manholes, to detail.
K23 | IN SITU CONCRETE CHAMBERS
K232 | Depth 1.5 - 2 m
K232.1 | Provide all materials and construct Reinforced concrete WASHOUT VALVE Chamber, internal dimensions 1200mm x 1200mm. Include for supply and fixing of removable reinforced concrete cover, mild steel frame, lifting / opening mechanism, plastic coated step irons, Vents, drainage system etc . All as specified and as detailed on Drawing No. M430/SD/03 | Nr | 10
K232.2 | Provide all materials and construct Reinforced Concrete AIR VALVE Chamber, internal dimensions 2400mm x 2000mm. Include for supply and fixing of removable reinforced concrete cover, mild steel frame, lifting / opening mechanism, plastic coated step irons, Vents, drainage system, etc . All as specified and as detailed on Drawing No. M430/SD/02 | Nr | 4
K232.2 | Provide all materials and construct Reinforced Concrete GATE VALVE Chamber, internal dimensions 1800mm x 1700mm. Include for supply and fixing of removable reinforced concrete cover, mild steel frame, lifting / opening mechanism, plastic coated step irons, Vents, drainage system, etc . All as specified and as detailed on Drawing No. M430/SD/05-1 | Nr | 2
K232.2 | Provide all materials and construct Reinforced Concrete ELECTROMANGETIC WATER METER Chamber, internal dimensions 2300mm x 2000mm. Include for supply and fixing of removable reinforced concrete cover, mild steel frame, lifting / opening mechanism, plastic coated step irons, Vents, drainage system, etc . All as specified and as detailed on Drawing No. M430/SD/06 | Nr | 1
K233 | Depth 2-2.5 m
K233.1 | Provide all materials and construct Reinforced concrete WASHOUT VALVE Chamber, internal dimensions 1200mm x 1200mm. Include for supply and fixing of removable reinforced concrete cover, mild steel frame, lifting / opening mechanism, plastic coated step irons, Vents, drainage system etc . All as specified and as detailed on Drawing No. M430/SD/03 | Nr | 16
PAGE TOTAL CARRIED TO BILL COLLECTION SHEET
K233.2 | Provide all materials and construct Reinforced Concrete AIR VALVE Chamber, internal dimensions 2400mm x 2000mm. Include for supply and fixing of removable reinforced concrete cover, mild steel frame, lifting / opening mechanism, plastic coated step irons, Vents, drainage system, etc . All as specified and as detailed on Drawing No. M430/SD/02 | Nr | 2
K234 | Depth 2.5-3 m
K234.1 | Provide all materials and construct Reinforced Concrete AIR VALVE Chamber, internal dimensions 2400mm x 2000mm. Include for supply and fixing of removable reinforced concrete cover, mild steel frame, lifting / opening mechanism, plastic coated step irons, Vents, drainage system, etc . All as specified and as detailed on Drawing No. M430/SD/02 | Nr | 22
K234.2 | Provide all materials and construct Reinforced concrete LINE VALVE Chamber, internal dimensions not exceeding 2700mm x 2400mm. Include for supply and fixing of removable reinforced concrete cover, mild steel frame, lifting / opening mechanism, mild steel CAT Ladder, Vents, drainage system etc . All as specified and as detailed on Drawing No. M430/SD/05 | Nr | 1
K234.2 | Provide all materials and construct Reinforced concrete LINE VALVE Chamber, internal dimensions not exceeding 3500mm x 2400mm. Include for supply and fixing of removable reinforced concrete cover, mild steel frame, lifting / opening mechanism, mild steel CAT Ladder, Vents, drainage system etc . All as specified and as detailed on Drawing No. M430/SD/05 | Nr | 1
K235 | Depth 3-3.5 m
K235.1 | Provide all materials and construct Reinforced concrete LINE VALVE Chamber, internal dimensions not exceeding 2700mm x 2400mm. Include for supply and fixing of removable reinforced concrete cover, mild steel frame, lifting / opening mechanism, mild steel CAT Ladder, Vents, drainage system etc . All as specified and as detailed on Drawing No. M430/SD/05 | Nr | 2
K235.2 | Provide all materials and construct Reinforced Concrete AIR VALVE Chamber, internal dimensions 2400mm x 2000mm. Include for supply and fixing of removable reinforced concrete cover, mild steel frame, lifting / opening mechanism, plastic coated step irons, Vents, drainage system, etc . All as specified and as detailed on Drawing No. M430/SD/02 | Nr | 9
K235.3 | Provide all materials and construct Reinforced Concrete ELECTROMAGNETIC METER Chambers internal dimensions 1500mm x 1300mm. Include for supply and fixing of removable reinforced concrete cover, mild steel frame, lifting / opening mechanism, mild steel CAT Ladder, vents, drainage system, etc. All as specified and as detailed on Drawing No. M430/SD/06 | Nr | 2
K235.4 | Provide all materials and construct Reinforced Concrete GATE VALVE Chambers internal dimensions 1600mm x 1300mm. Include for supply and fixing of removable reinforced concrete cover, mild steel frame, lifting / opening mechanism, mild steel CAT Ladder, vents, drainage system etc . All as detailed on Drawing No. M430/SD/05 | Nr | 2
PAGE TOTAL CARRIED TO BILL COLLECTION SHEET
K236 | Depth 3.5-4 m
K236.1 | Provide all materials and construct Reinforced Concrete AIR VALVE Chamber, internal dimensions 2400mm x 2000mm. Include for supply and fixing of removable reinforced concrete cover, mild steel frame, lifting / opening mechanism, plastic coated step irons, Vents, drainage system, etc . All as specified and as detailed on Drawing No. M430/SD/02 | Nr | 1
K236.2 | Provide all materials and construct Reinforced concrete LINE VALVE Chamber, internal dimensions not exceeding 2700mm x 2400mm. Include for supply and fixing of removable reinforced concrete cover, mild steel frame, lifting / opening mechanism, mild steel CAT Ladder, Vents, drainage system etc . All as specified and as detailed on Drawing No. M430/SD/05 | Nr | 1
K236.3 | Provide all materials and construct Reinforced Concrete ELECTROMAGNETIC METER Chambers internal dimensions 2400mm x 2800mm. Include for supply and fixing of removable reinforced concrete cover, mild steel frame, lifting / opening mechanism, mild steel CAT Ladder, vents, drainage system, etc. All as specified and as detailed on Drawing No. M430/SD/06 | Nr | 1
K237 | Depth exceeding 4 m
K237.1 | Provide all materials and construct Reinforced Concrete AIR VALVE Chambers, internal dimensions 2400mm x 2000mm. Include for supply and fixing of removable reinforced concrete slab / cover, mild steel frame, lifting / opening mechanism, step irons, compacted granular fill, vents, drainage system, rendering of exposed blockwork etc . All as specified and as detailed on Drawing No. M430/SD/02 | Nr | 5
K237.2 | Provide all materials and construct Reinforced concrete LINE VALVE Chamber, internal dimensions not exceeding 2700mm x 2400mm. Include for supply and fixing of removable reinforced concrete cover, mild steel frame, lifting / opening mechanism, mild steel CAT Ladder, Vents, drainage system etc . All as specified and as detailed on Drawing No. M430/SD/05 | Nr | 2
K25 | PRECAST CONCRETE CHAMBERS
K254 | Depth 2.5-3m
K254.1 | Provide all materials and construct Precast Concrete WASHOUT VALVE Surface Box. Include for supply and fixing of Class 30 PCC unit, surface box and lockable cover, 1000x1000x250mm Class 25/20 RC protection slab, compacted granular fill, OD 160mm uPVC pipe sleeve, length not exceeding 3m, etc. all as detailed on Drawing . No. M430/SD/04 | Nr | 3
K255 | Depth 3-3.5m
K255.1 | Ditto but depth 3-3.5m, OD 160mm uPVC pipe sleeve, length not exceeding 3.5m | Nr | 7
PAGE TOTAL CARRIED TO BILL COLLECTION SHEET
K256 | Depth 3.5-4m
K256.1 | Ditto but depth 3.4-4m, OD 160mm uPVC pipe sleeve, length not exceeding 4m | Nr | 5
K257 | Depth exceeding 4m
K257.1 | Ditto but depth exceeding 4m, OD 160mm uPVC pipe sleeve, length exceeding 4m | Nr | 3
K6 | CROSSINGS
K63 | Under-River Crossings, Width exceeding 10m
Details as per Dwg No. M430/SD/10
K633 | Pipe bore 900-1800mm
Note: Items for work shall include:
K633.1 | Excavation for foundation in river/stream beds depth n.e 4.0m, preparation of surfaces, disposal of excavated material, upholding sides of excavation, backfilling and removal of redundant services, all as per Dwg No. M430/SD/10, Nominal Bore 1000mm (Provisional) | m | 520
K633.2 | Extra over item K633.1 for excavation in rock, depth n.e. 4.0m including preparation of trenches (No blasting permitted) (Provisional)
K633.2.1 | Class 'A' | m3 | 40
K633.2.2 | Class 'B' | m3 | 450
K633.2.3 | Class 'C' | m3 | 250
K633.3 | Transport from Site Store, Install, Test and Commission DN 1000mm ferrous pipes on under-river Crossings, jointing to specifications | m | 520
K633.4 | Supply 'Denso Tape' wrapping or approved equivalent. Bidder to include for wrapping at welded joints on the ferrous pipe in two layers as directed by the Engineer. | m² | 3270
K633.5 | Backfill the trench with concrete Class 15/20 surround, include for vibrating as directed by the Engineer all as per Dwg No. M430/SD/10 | m3 | 985
K633.6 | Backfill the trench with approved selected excavated material compacted in 300mm layers | m3 | 550
K633.7 | Backfill trench with approved imported compacted granular material compacted in 300mm layers | m3 | 825
Gabion Works
K633.8 | Provide all materials and carry out laying of 2m x 1m x 1m Gabions, wire minimum size 5mm or as specified. Gabion boxes to be laid in stretches with 0.5m overlap, mesh wire to be galvanised and minimum diameter 5mm. Include for tying of adjacent gabions with approved wire and 16mm dia anchor rods to suit site conditions (Provisional) | Nr | 1250
PAGE TOTAL CARRIED TO BILL COLLECTION SHEET
K633.9 | Provide all materials and carry out laying of 0.23 - 0.5m thick gabion mattresses, mesh wire to be galvanised and of minimum diameter 5mm. Include for tying of adjacent gabions with approved wire and 16mm dia anchor rods to suit site conditions (Provisional) | m2 | 1620
K633.10 | Provide and place rockfill to gabions and mattresses | m3 | 3500
K633.11 | Extra over for infilling of gabions with Class 15 mass concrete | m3 | 110
K633.12 | Formwork
Provide and fix shutterings including propping, strutting and striking, all as specified.
Sawn Formwork - Class F1 Finish
K633.12.1 | Vertical Sides of Concrete in foundation | m2 | 2310
K633.13 | Method Related Charges
K633.13.1 | Allow for diverting River/Stream including construction of cofferdam etc., for river crossing works and reinstate after construction. The River/Stream to be kept operational during construction, width 3 - 6m | Nr | 2
K633.13.2 | Allow for keeping excavation free of water which may occur through ground water seepage, rain or other means. | Item | LS
K633.13.3 | Allow for any other method related charges the Bidder feels may be required. These should be indicated below with pricing of each item.
| i) | Item | L.S
| ii) | Item | L.S
K7 | Reinstatement
K733.3 | Breaking up, temporary and permanent reinstatement of MURRAM road with 300mm thick well graded stabilised gravel with 3% cement base compacted in 150mm thick layers using an 8-10 tonne roller and 150mm deep approved compacted hardcore to the satisfaction of the Engineer. Nominal pipe bore n.e. 1800mm. all as per Dwg No. M430/SD/12. Rates quoted shall be deemed to include for costs incurred on traffic control, signage and safety measures during execution of the works. | m | 800
K743.1 | Breaking up temporary and permanent reinstatement of UNPAVED FOOTPATHS. Pipe bore 900mm - 1800mm all as per Dwg No. M430/SD/12 | m | 400
K8 | Other Pipework Ancillaries
K821 | Marker Posts on Pipeline alignment
K821.1 | Supply and fix marker posts for water main route, road crossings, change of direction, air valves, washouts, and valve chambers. All in accordance with drawings and specifications | Nr | 320
K822 | Pipeline Wayleave Monumentation
K822.1 | Supply and Install wayleave Boundary Indicator Posts at edges of acquired Pipeline Wayleave, to mark full extent of the pipeline wayleave. Wayleave Boundary Indicator Posts details as per drawings, to be installed at approx. intervals of 200m. | Nr. | 300
PAGE TOTAL CARRIED TO BILL COLLECTION SHEET
Wash-out Outfall Rising Pipe
K87 | Provide all materials, fabricate and install washout chamber outfall rising pipe as detailed in drg. No. M430/SD/03. Rate to include for supply of all fittings, jointing, installation and connection to washout tee and valve. | Nr. | 30
K88 | Removal and Reinstatement of Existing Hedges, Fences, Walls and Drains
K88.1 | Allow for removal of existing HEDGES and reinstating these after laying of the water mains is completed. (Provisional) | m | 500
K88.2 | Allow for breaking up of existing masonry perimeter WALLS approx. 2.5m high, with concrete columns at approx. 3m intervals, and reinstatement after laying of water mains is completed.(Provisional) | m | 20
K88.3 | Allow for breaking up of existing FENCES, including but not limited to chain link fence, barbed wire fence, timber, iron sheet, electric fence, etc., and reinstating these after construction of the water mains is completed. | m | 250
K88.4.1 | Allow for breaking up of existing UNLINED EARTH DRAINS and reinstating these after construction of the water mains is completed. Include for provision of diverting the drains or water ways and keeping them operational during construction. Depth of Drain n.e. 3m (See Drg. No. M430/SD/19) (Provisional) | m | 500
K88.4.2 | -Ditto - but for existing STONE-PITCHED OPEN DRAINS, depth n.e. 3.0m (See Drg. No. M430/SD/19) (Provisional) | m | 50
CLASS L:- PIPEWORK - SUPPORTS AND PROTECTION, ANCILLARIES TO LAYING AND EXCAVATION
L1 | Extras to excavation and backfilling (Provisional)
L11 | In pipe trench and chambers
L111.1 | Excavation in trench for rock class "A" | m³ | 1200
L111.2 | Excavation in trench for rock class "B" | m³ | 18000
L111.3 | Excavation in trench for rock class "C" | m³ | 10000
Note:- Blasting is NOT permitted for Item L11
L5 | Surrounds
L52 | Provide, transport to site and place selected excavated granular fill and compact in bed and surround to pipes as specified and where directed by the Engineer |  |  |  |  | In areas where excavated material is unsuitable, but can be selected from other sections of the trench
L525 | To pipes nominal bore: 900 - 1200 mm | m | 17484
L53 | Provide, transport to site and place imported granular fill and compact in bed and surround to pipes as specified and where directed by the Engineer |  |  |  |  | Backfilling above pipe zone is included in Item I4. (Random backfilling with excavated material
L535 | To pipes nominal bore: 900 - 1200 mm | m | 11946
PAGE TOTAL CARRIED TO BILL COLLECTION SHEET
L54 | Provide all materials, transport to site and place mass concrete class 15/20 in bed and surround to pipes under road crossings and on shallow pipeline sections as directed by the Engineer. Include for provision, fixing and dismantling of all formwork, vibration of concrete etc. all as per Dwg No. M430/SD/13
L545 | To pipes nominal bore: ne 900 - 1200 mm | m | 800
L7 | Concrete Support, Thrust Blocks, Stools and Anchor Blocks |  |  |  |  | In case of Welded Steel Pipes, only require blocks will be used, eg. at Flanged Tees, etc. That's why the item is provisional
| Details as per Dwg No. M430/SD/08 - 09 (Provisional) |  |  |  |  | Standard Design of Thrust Blocks
Rates to include for excavation, formwork, provision and placing of concrete, backfilling etc.
Class 20/20 Mass Concrete
NOTE:- The work includes pipe and fitting fixing
L73 | Volume:- 0.2 - 0.5 m³
L731 | To pipes nominal bore: not exceeding 200mm | Nr
L73 | Volume:- 0.2 - 0.5 m³
L734 | To pipes nominal bore: 600 -900mm | Nr | 102
L74 | Volume:- 0.5 - 1 m³
L745 | To pipes nominal bore: 900 -1200mm | Nr | 13
L75 | Volume:- 1 - 2 m³
L755 | To pipes nominal bore: 900 -1200mm | Nr | 11
L76 | Volume:- 2 - 4 m³
L764 | To pipes nominal bore: 600 -900mm | Nr | 145
L77 | Volume:- 4 - 6 m³
L775 | To pipes nominal bore: 900 -1200mm | Nr | 655
L78.1 | Volume:- 6- 10 m³
L785.1.1 | To pipes nominal bore: 900 -1200mm | Nr | 12
L78.2 | Volume:- exceeding 10m³
L785.1.2 | Volume 10-20m3 to pipes nominal bore: 900 -1200mm | Nr | 13
L785.1.3 | Volume 30-40m3 to pipes nominal bore: 900 -1200mm | Nr | 2
CLASS V: PAINTING
V310 | Allow for cleaning and painting with 3 coats of approved epoxy paint all exposed Pipework, Fittings, Valves, etc. | m2 | 5470
CLASS X: MISCELLANEOUS WORKS
X4 | Gabion Works
X411 | Supply and Install approved Gabion Boxes, size 2m x 1m x 1m mesh wire minimum size 5mm diameter laid in cascading stacks around R.C. piers on aerial crossings, and or as specified, Gabion boxes to be instructed by the Engineer on site, all as directed. Rate to include for supply and packing of approved hardcore into gabion boxes, all to Engineer's approval, as shown on Drg. No. M430/SD/16. | Nr | 900
X421 | Ditto - but Gabion Mattresses, thickness 500mm mesh wire 5mm diameter | m2 | 1200
PAGE TOTAL CARRIED TO BILL COLLECTION SHEET
X990 | EROSION CONTROL AND PROTECTION MEASURES (PROVISIONAL)
X990.1 | Provide all materials and construct mass concrete EROSION CHECKS on steep sloped as specified and according to details given in Drg. No. M430/SD/10. | Nr. | 850
X990.2 | Provide all materials and carry out hydraulic mulch Grass seeding to slopes as specified on the drawings, all to Engineer's approval. | m2 | 4500
X990.3 | Supply and plant approved grass on slopes and maintainance until it takes root to the satisfaction of the Engineer. Rate to include for excavation of cut-off drains to divert run-off water from pipe trench alignment. | m2 | 9850
X991 | HEADWALLS, CASCADES AND OUTFALL CHAMBERS
Details as per Dwg No. M430/SD/03-04 (Provisional Quantities)
X991.1 | Excavation
The rates shall include for all strutting, shuttering, stabilising the excavation and preparation of excavated surfaces to receive permanent work.
Excavate for foundations, part backfill after construction and remainder, cart away to tips or use as fill on site, all as directed by the Engineer. Tips to be identified by the Contractor in liaison with the Local Authority.
X991.1.1 | Maximum depth n.e. 1.0m | m3 | 220
X991.1.2 | -Ditto - depth 1.0 to 1.5m | m3 | 230
X991.1.3 | -Ditto - depth exceeding 1.5m | m3 | 350
X991.1.4 | E.O. excavation items for excavation in rock Class 'A' (Provisional) | m3 | 16
X991.1.5 | -Ditto - for excavation in rock Class 'B' (Provisional) | m3 | 240
X991.1.6 | -Ditto - for excavation in rock Class 'C' (Provisional) | m3 | 130
X991.2 | Concrete Works
Provide, mix and place concrete as directed
X991.2.1 | Plain concrete Class 15/20 in 50mm blinding layer under bases/treads. | m2 | 290
X991.2.2 | Vibrated, Reinforced Concrete Class 25/20 in:-
X991.2.2.1 | Footings | m3 | 7
X991.2.2.2 | Bases | m3 | 37
X991.2.2.3 | Walls | m3 | 37
X991.2.2.4 | Treads | m3 | 2
X991.2.2.5 | Risers | m3 | 7
X991.2.2.6 | Roof Slabs | m3 | 14
PAGE TOTAL CARRIED TO BILL COLLECTION SHEET
X991.3 | Reinforcement
Provide and fix high tensile steel reinforcement to SRN 127 including cutting, bending, propping, with spacers and tying as specified.
X991.3.1 | All diameters | kg | 21700
X991.4 | Formwork
Provide and fix shuttering including propping, strutting and striking all as specified.
(i) Vertical Formwork - Class F1 Finish
X991.4.1 | Sides of 200mm treads/ bases/ risers | m | 912
X991.4.2 | Sides of footings - width n.e. 0.2m | m | 68
X991.4.3 | Sides of footings - width exceeding 0.2m | m² | 38
X991.4.4 | External faces of chamber walls/ headwalls - width exceeding 0.2m | m² | 530
(ii) Vertical Formwork - Class F2 Finish
X991.4.5 | Sides of 200mm roof slabs and walls | m | 292
X991.4.6 | Internal faces of chamber walls/ headwalls etc | m² | 370
(iii) Horizontal Formwork - Class F2 Finish
X991.4.7 | Soffites of roof slabs and walls | m² | 62
X991.5 | Walling
Natural Stone Block Walling, Medium Chisel Dressed, Reinforced with 20 swg Hoop Iron at Every Alternate Course, and Bedded, Jointed and Pointed in Cement Mortar (1:4):-
X991.5.1 | 200 mm Walling | m2 | 83
X991.6 | Plastering
12.5mm Thick Gauged Cement Plaster as per specifications on:
X991.6.1 | Natural stone block walling and other surfaces | m2 | 166
X991.7 | Miscellaneous Works
X991.7.1 | Provide for and fix plastic coated step irons in rising outfall chambers for Washouts as specified by the Engineer. Details of chamber are in Dwg Nr. M430/SD/04 | Nr | 110
X991.7.2 | Provide Precast Reinforced Concrete Covers size 600 x 600 x 50mm thick to the rising outlet Chambers. | Nr | 12
X991.8 | Method Related Charges
X991.8.1 | Allow for River diversion, for construction of W.O outfall structures including construction of cofferdam etc., for River crossing works and reinstate after construction. The River / Waterway to be kept operational during construction. The Bidder to submit method statement with Bid for execution of these works. | Item | L.S
X991.8.2 | Method related charges for keeping excavation free of water which may occur through ground water seepage, rain or other means. | Item | L.S
PAGE TOTAL CARRIED TO BILL COLLECTION SHEET
X991.8.3 | Allow for any other method related charges the Bidder feels may be required. These should be indicated below with pricing of each item.
| i) | Item | L.S
| ii) | Item | L.S
X992 | AERIAL CROSSINGS ON PIERS - 14Nr Crossings
Details as per Dwg Nos. M430/SD/13
Pipe Nominal Bore n.e 900 - 1800mm
X992.1 | Excavation
The rates shall include for all strutting, shuttering, stabilising the excavation faces and preparation of excavated surfaces to receive permanent work.
Excavate for pier footings on aerial Crossings, part backfill after construction and remainder, cart away to approved tips or use as fill on site, all as directed by the Engineer. Tips to be identified by the Contractor in liaison with the Local Authority.
X992.1.1 | Maximum depth n.e. 1.5m | m3 | 1368
X992.1.2 | -Ditto - depth 1.5 to 2.0m | m3 | 466
X992.1.3 | -Ditto - depth exceeding 2.0m | m3 | 445
X992.1.4 | E.O. excavation items for excavation in rock Class 'A' (Provisional) - Blasting not permitted | m3 | 50
X992.1.5 | -Ditto - for excavation in rock Class 'B' (Provisional) - Blasting not permitted | m3 | 770
X992.1.6 | -Ditto - for excavation in rock Class 'C' (Provisional) - Blasting not permitted | m3 | 330
X992.2 | Concrete Works
Provide, mix and place concrete as directed Note: Concrete Works at the Mwache Creek Crossing to be carried out using Sulphate Resistant Cement as specified in SRN 104 of the Specifications.
X992.2.1 | Plain concrete Class 15/20 in 75mm blinding layer under pier footings. | m2 | 869
X992.2.2 | -Ditto- but 75mm thick, on exposed surface of gabions | m2 | 936
X992.2.3 | Vibrated, Reinforced Concrete Class 25/20 in:-
X992.2.3.1 | Footings | m3 | 435
X992.2.3.2 | Piers | m3 | 897
X992.3 | Reinforcement
Provide and fix high tensile steel reinforcement to SRN 127 including cutting, bending, propping, with spacers and tying as specified.
X992.3.1 | 12mm and under | kg | 74592
X992.3.2 | 16mm and over | kg | 111888
PAGE TOTAL CARRIED TO BILL COLLECTION SHEET
X992.4 | Formwork
Provide and fix shuttering including propping, strutting and striking all as specified.
(i) Vertical Formwork - Class F1 Finish
X992.4.1 | Sides of 500mm footings | m2 | 670
X992.4.2 | Sides of piers in foundations | m2 | 1265
(ii) Vertical Formwork - Class F2 Finish
X992.4.3 | Outer faces of column piers - width 1.0m - 3.0m | m2 | 1999
(iii) Sloping Formwork - Class F2 Finish
X992.4.4 | Sloping face of column head | m2 | 2267
X992.5 | Pipe Support Details
Provide all materials, fabricate and install 75mm wide x 15mm thick flat GMS Strap on pipes on piers at Aerial Crossings; Rate to include for supply and installation of Rag Bolts, Rubberoid layers, etc. all as detailed in Drg. No. M430/SD/13; to Engineer's approval.
X992.5.1 | DN 1000 | Nr | 174
X992.6 | Design and Construction of Piling Works for Mwache Creek Crossing
X992.6.1 | Allow a provisional sum of Kshs. 25,000,000 (Kenya Sillings Twenty Five Million) for carrying out detailed Geotechnical Investigation and Detailed Design of the Mwache Creek Crossing Piling System. The pile design shall take into consideration the soil conditions at the creek crossing, structural requirements of the pipeline crossing and any other anticipated loads and environmental conditions, and shall comply with all relevant codes, standards and specifications. Rate to include for preparation of Geotechnical Invstigation Report for the creek crossing, pile design calculations and drawings, pile load test procedures and design specifications for piling works, all to the Engineer's Approval. | Item | PS |  | 25000000
X992.6.2 | Provide all materials and install cylindrical driven and cast-in-situ friction piles, diameter 150mm; to receive pier bases, pile depth ranging from 12m to 20m, minimum steel pile pipe thickness 8mm, all as per approved designs prepared under item X992.6.1 above and as directed by the Structural Engineer on site. Rate to include for provision and placing of vibrated class 25/20 Reinforced Concrete internally in the steel piles, etc., estimate minimum steel reinforcement per pile 5Nr. D12 bars with circular links at 150mm c/c (to be confirmed by the detailed design). Minimum No. of piles per pier is 4Nr. Works for construction of Piers and pipeline installation works measured seperately. Item applicable for Mwache Creek Crossing only. | Nr | 130
X992.6.3 | Allow for provision and use of berges mounted with piling rigs, etc., or any other alternative method for execution of works within the creek approved by the engineer | Item | L.S
X992.6.4 | Allow any other Method Related Charges for construction of piles and piers with pier bases on piles in submerged conditions, and installation of DN 1000 Steel Pipes on Piers across the creek. Rate to include for all method related charges for working within the flooded creek crossing at heights. | Item | L.S
X992.7 | Method Related Charges (Applicable to all River Crossings)
X992.7.1 | Allow for River Diversion Works, including construction of cofferdams etc., for river crossing works and reinstate after construction. The Rivers / Waterways to be kept operational during construction. Bidder to submit method statement with Bid for execution of these works. | Item | L.S
X992.7.2 | Method related charges for keeping excavations free of water which may occur through ground water seepage, rain or other means. | Item | L.S
X992.7.3 | Allow for any other method related charges the Bidder feels may be required. These should be indicated below with pricing of each item.
| i) | Item | L.S
| ii) | Item | L.S
PAGE TOTAL CARRIED TO BILL COLLECTION SHEET
X993 | Miscellaneous Works (Provisional)
X993.1 | Allow Provisional Sum for other Miscellaneous Works that may be required on site to be carried out as directed by the Engineer. | Item | P.S | 20000000 | 20000000
X994 | CATHODIC PROTECTION FOR STEEL PIPES AND FITTINGS:
NOTE: THIS ITEM SHOULD ONLY BE PRICED IF THE BIDDER HAS QUOTED FOR STEEL PIPES AND FITTINGS. BIDDERS QUOTING FOR DUCTILE IRON PIPES AND FITTINGS SHOULD NOT PRICE FOR THESE ITEMS.
X994.1 | Carry out Detailed Design of Cathodic Protection system for the DN 1000/900 Transmission Pipeline to the South Mainland, total length of pipeline 27.8km. Rate to include for all requisite confirmatory field tests and analysis such as soil resistivity, current drain, natural potential survey, etc., system design and approval.Design to be based on impressed current Cathodic Protection system. | Item | L.S
X994.2 | Supply of all required materials, Installation, Testing and commissioning of the Impressed Current Cathodic Protection system on Steel South Mainland Transmission Pipeline as per approved design, total length of pipeline not exceeding 27.8km. | Item | L.S
X994.3 | Bi-monthly assistance by the Specialized Sub-Contractor to verify the performance of the Cathodic Protection System, to carry out the appropriate maintenance if needed and to train MOWASSCO staff on these issues, during the Defects Liability Period. | Item | 6
X995 | Interconnection to Existing Marere Pipeline
X995.1 | Allow for identification,exposing,cutting,backfiling and reinstatement after installation of fittings and pipework for interconnection of the existing Marere Pipeline to the proposed South Mainland pipeline. Pipework and fittings provision and installation has been measures in the respective bill items. Pipe Nominal bore DN500 | Item | L.S
X996 | WRAPPING OF STEEL FITTINGS AND JOINTS
NOTE: THIS ITEM SHOULD ONLY BE PRICED IF THE BIDDER HAS QUOTED FOR STEEL PIPES AND FITTINGS. BIDDERS QUOTING FOR DUCTILE IRON PIPES AND FITTINGS SHOULD NOT PRICE FOR THESE ITEMS.
X996.1 | Provide all materials and wrap all Steel Fittings with approved Petrolatum Tape such as Denso Tape or appoved equivalent, including an outwrap applied with atleast 55% overlap. Wrapping to be applied on all Steel Fittings without 3LPE coating, including Bends, Tees, Short Pieces, Tapers, couplings, etc. Application to be carried out as per Manufacture's Specifications, to the Engineer's Approval | m2 | 2500
X997 | Allow a provisional sum of Kshs. 100 Million (One Hundred Million Kenya Shillings) for Rehabilitation of existing DN 500 Steel Pipeline within the Mwache Creek Crossing. Works shall include carrying out geotechnical investigations, design and construction of R.C. Piers on Piles, removal of existing pipes and fittings across the creek, supply and installation of new DN 500 pipes and fittings, testing and commissioning of the pipeline. | Item | PS | 100000000 | 100000000
PAGE TOTAL CARRIED TO BILL COLLECTION SHEET
Note on A565: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: to be removed

## Collection Sheet Bill No. 3.2
IMPROVEMENT OF DRINKING WATER AND SANITATION SYSTEMS IN MOMBASA: MWACHE CKE 1103
LOT 1: CONSTRUCTION OF THE MWACHE TWIN TRUNK MAIN (TM1), SOUTH MAINLAND TRANSMISSION PIPELINE AND DONGO KUNDU RESERVOIR
BID No. CWWDA/AFD/PQ/W4/2022-2023
BILL No. 3.2 - SOUTH MAINLAND WATER TRANSMISSION PIPELINE (LINE SM)
PIPELINE CONSTRUCTION
Amount
(Kshs.)
Page Total, Page 1 of 20
Page Total, Page 2 of 20
Page Total, Page 3 of 20
Page Total, Page 4 of 20
Page Total, Page 5 of 20
Page Total, Page 6 of 20
Page Total, Page 7 of 20
Page Total, Page 8 of 20
Page Total, Page 9 of 20
Page Total, Page 10 of 20
Page Total, Page 11 of 20
Page Total, Page 12 of 20
Page Total, Page 13 of 20
Page Total, Page 14 of 20
Page Total, Page 15 of 20
Page Total, Page 16 of 20
Page Total, Page 17 of 20
Page Total, Page 18 of 20
Page Total, Page 19 of 20
Page Total, Page 20 of 20
Bill No. 3.2 Total Exclusive of VAT carried to Summary Sheet |  | 0 | 0
0
0
|  | 692744583.3289 | #REF!

## Bill No. 4.1
IMPROVEMENT OF DRINKING WATER AND SANITATION SYSTEM IN MOMBASA: MWACHE CKE 1103
LOT 1: CONSTRUCTION OF THE MWACHE TWIN TRUNK MAIN (TM1), SOUTH MAINLAND TRANSMISSION PIPELINE AND DONGO KUNDU RESERVOIR
BID No. CWWDA/AFD/PQ/W4/2022-2023
BILL No. 4.1 - DONGO KUNDU RESERVOIR (28,000 m3 CAPACITY)
ITEM | DESCRIPTION | UNIT | QUANTITY | RATE | AMOUNT
No. |  |  |  | (Kshs) | (Kshs)
NOTES:
The Proposed Dongo Kundu Reservoir comprises of 2Nr. RC Water Storage Tanks, each of 14,000 m³ Capacity, with a combined capacity of 28,000 m³.
| This Bill of Quantities (Bill No. 4.1) covers the construction of the Proposed 2Nr. RC Tanks. Other Works within the Reservoir Site are measured separately under Bill Nos. 4.2 and 4.3. | [5 empty] | RATE (Kshs) | Reference | Factor
1 | General
1.1 | Water tightness testing of the 2Nr. R.C. Tanks in accordance with specifications, all to the satisfaction of the Engineer. Include for provision of water from approved source, and safe disposal after testing. | Item | L.S |  |  |  | 1500000 |  | 1.3
1.2 | Cleaning and sterilization of the 2Nr. RC Tanks in accordance with specifications. Rate to include for provision of water, all required chemicals and carrying out relevant water quality tests as well as safe disposal of used water, all to the Engineer's approval. | Item | L.S |  |  |  | 1200000 |  | 1.3
1.3 | Pressure testing, flushing and sterilization of all pipework (inlet pipework, outlet pipework, washout and overflow pipework), etc., for the 2Nr. Tanks, all in accordance with specifications. Rate to include for provision of water, all required chemicals and carrying out relevant water quality tests as well as safe disposal of used water, all to the Engineer's approval. | Item | L.S |  |  |  | 1000000 |  | 1.3
Compaction Tests (Provisional)
1.4 | Allow for carrying out Compaction tests at formation level of the 2Nr. RC Tanks using the Sand Displacement method or other approved In-situ method. Rate to include for provision of all apparatus, Equipment and Materials and carrying out the test as per standard procedures. Test to be carried out in at least 10Nr. locations, to be selected by the Engineer, within the reservoir bases. | Item | L.S
1.5 | Allow for compaction of formation surfaces deemed to be inadequate upon compaction tests under Item 1.4 above. Rate to include for provision of an adequate capacity vibrating roller compaction equipment and compaction of formation levels to a relative density of 98% MDD, all as per specifications. | m2 | 5600 |  |  | 0
2 | Earthworks
Note: Excavation quantities to be measured from stripped surface / reduced ground levels. Top soil stripping and Mass Excavation for site is measured separately under Bill No 4.3 (Site and Ancillary Works)
Rates shall include for all strutting, shuttering, stabilizing the excavation faces and keeping the excavation free of water by pumping, bailing or other means.
Excavate for the 2Nr. R.C. Tanks from stripped surface / reduced ground levels, part backfill with approved selected material after construction and remainder cart away to approved tips or use as fill on site, all as directed. Tips to be identified by the Contractor in liaison with local authorities.
2.1 | Maximum depth of excavation n.e. 1.0m | m3 | 6600
PAGE TOTAL CARRIED TO COLLECTION SHEET
2.2 | -Ditto - but excavation depth 1.0m to 2.0m | m3 | 6600
2.3 | -Ditto - but excavation depth 2.0m to 3.0m | m3 | 3600
2.4 | -Ditto - but excavation depth 3.0m to 6.0m | m3 | 100
2.5 | Allow for trimming of excavated surface to formation level of Reservoir, to receive plain concrete blinding. | m2 | 6600
2.6 | Extra Over items 2.1 to 2.5 for excavation in rock class 'A', blasting not permitted (Provisional) | m3 | 80
2.7 | -Ditto- but for excavation in rock class 'B', blasting not permitted (Provisional) | m3 | 2320
2.8 | -Ditto- but for excavation in rock class 'C', blasting not permitted (Provisional) | m3 | 980
2.9 | Provide, place and compact approved imported murram, compacted in 150mm thick layers in making-up levels where unsuitable material is identified, to compaction densities as directed by the Engineer on site, all in accordance to specifications. Contractor to identify suitable borrow pits as source of material. Contractor's Rate to include for compaction tests, transport, provision of compaction equipment, water, etc. and other related charges. | m3 | 3600
2.1 | Provide and place approved hardcore packing, hand-packed and compacted to Engineer's approved, maximum 300mm thick layer. Rate to include for provision, packing and compaction. | m3 | 1800
3 | Concrete Works
Provide all materials, mix and place Concrete as directed.
3.1 | Provide and place 75mm thick blinding concrete class 15/20 under Base Slabs and Foundations. | m2 | 6600
Guaranteed Strength Reinforced Concrete Class 25/20, maximum aggregate as specified in:-
3.2 | External Wall Bases including key and splay | m3 | 1200
3.3 | Internal Partition Wall Bases | m3 | 200
3.4 | Base Slab and Sumps | m3 | 840
3.5 | Bases to Columns | m3 | 100
3.6 | Bases to Internal Baffle Walls | m3 | 30
3.7 | Main External Walls | m3 | 960
3.8 | Internal Partition Walls | m3 | 200
3.9 | Baffle Walls | m3 | 240
3.1 | Columns, including top flared heads | m3 | 90
3.11 | 250mm thick Roof Slabs, including all Upstands | m3 | 1530
PAGE TOTAL CARRIED TO COLLECTION SHEET |  |  |  |  | 0
Class 20/20 Mass Concrete, maximum aggregate as specified in:-
3.12 | 300mm thick Mass Concrete Pad above and below Base Slab at Inlet Pipe discharge point. | m3 | 5
3.13 | Surround to pipework and thrust blocks. | m3 | 100
4 | Steel Reinforcement
Provide and fix high tensile reinforcement to BS 4461, including for cutting, bending, propping with spacers and tying as specified:-
4.1 | Reinforcement; all diameters | Ton | 810
4.2 | Fabric Mesh Reinforcement (BRC Class A252) | m2 | 4600
5 | Formwork
Provide all materials and fix shuttering, including propping, strutting and striking all as specified. Rate to include for formation of chamfers at exposed concrete edges.
i) Vertical Formwork Class F1 Finish
5.1 | External sides of base slab, width n.e. 0.3m | m | 1600
5.2 | Both sides of key, width 1 to 1.5m | m2 | 1000
2 | CLASS D: DEMOLITION AND SITE CLEARANCE
5.3 | External sides of washout and Outlet Pipe Sumps | m2 | 100
ii) Vertical Formwork Class F3 Finish
5.4 | Both sides of external walls, width n.e. 5.3m | m2 | 5600
5.5 | Both sides of internal partition wall base, width n.e. 0.5m | m2 | 600
5.6 | Both sides of internal partition wall, width n.e. 5.3m | m2 | 1120
5.7 | Both sides of baffle wall bases, width n.e. 0.25m | m | 1000
5.8 | Both sides of baffle walls, width n.e. 4.7m | m2 | 4000
5.9 | Sides of column bases, width n.e. 0.3m | m | 1000
5.1 | Sides of columns, width n.e. 0.3m | m | 3200
5.11 | Internal sides of washout and Outlet Pipe Sumps, width n.e. 1.5m | m2 | 100
5.12 | Both sides of overflow chambers, width n.e.1.3m | m2 | 60
5.13 | Outer side of roof slab and upstand, width n.e.0.6m | m2 | 280
5.14 | Inner side of roof upstand 300mm high | m2 | 160
5.15 | Inner sides of access manholes, width n.e. 0.6m | m2 | 64
5.16 | Outer sides of access manhole upstands 300mm high | m2 | 60
PAGE TOTAL CARRIED TO COLLECTION SHEET
iii) Sloping Formwork Class F3 Finish
5.17 | Splay of base slab | m2 | 840
5.18 | Splay in wall, width n.e. 0.3m | m | 1200
5.19 | Splay at column heads, width n.e. 0.5m | m2 | 200
5.2 | 100mm x 100mm chamfer at overflow chamber, width n.e. 0.1m | m | 412
5.21 | 20mm x 20mm fillet to form chamfer for all exposed concrete upstands, wall edges, column edges, etc., width n.e. 0.05m | m | 5600
iv) Horizontal Formwork Class F3 Finish
5.22 | Soffit of suspended slab | m2 | 7560
5.23 | Soffit of overflow chambers | m2 | 10
v) Box Outs, Rebates and Drip Mould
5.24 | Form 1200mm x 550mm void for overflow | Nr | 4
5.25 | 50mm x 50mm rebates on slabs for manhole covers | m | 140
5.26 | 12mm dia. half round fillet for drip mould round soffit of roof slab overhang | m | 560
5.27 | Extra over concrete works for boxouts for pipes nominal bore n.e 900mm and making good after installation of Inlet Pipework | Nr. | 4
5.28 | - Ditto-, but for 1020mm x 1020mm Access / Inspection Manholes | Nr. | 24
6 | Joints
i) Expansion Joints
6.1 | Form 20mm wide x 200mm deep expansion joint including for the following: a) 20mm x 20mm polysulphide sealant on upper face b) Non-absorbent compressible filler material c) 250mm Expadite Supercast Rearguard S PVC waterstop or similar approved | m | 450
ii) Contraction Joints a) In Base Slabs:
6.2 | Form partial contraction joint in Base Slab including for 20mm x 20mm polysulphide sealant on upper face and 200mm Expadite Supercast Rearguard R PVC waterstop or similar approved. | m | 900
b) In Wall Bases:
6.3 | Form full contraction joint in wall base including for 20mm x 20mm polysulphide sealant on upper face and 250mm Expadite Supercast Rearguard R PVC waterstop or similar approved. | m | 265
PAGE TOTAL CARRIED TO COLLECTION SHEET
c) In Walls:
6.4 | Form full contraction joint in wall including for 20mm x 20mm polysulphide sealant on upper face and 250mm Expadite Supercast water foil PVC waterstop or similar approved. | m | 40
iii) Construction Joints
a) In Roof Slabs:
6.5 | Form construction joints in roof slab including for 20mm x 20mm polysulphide sealant in upper face. | m | 700
b) In Walls:
6.6 | Form construction joint in wall including for 20mm x 20mm polysulphide sealant on inner face and 200mm wide PVC waterstop. | m | 1320
iv) Roof Slab / Walls joints
6.7 | Form roof slab / wall joint including for 13mm x 25mm polysulphide joint sealant on both faces, non-compressible joint filler and PSC rubber bearing 3KX or similar approved. | m | 700
Pipes, Fittings and Valves
7 | Supply, Transport to Site & Store in secure place including Jointing Material, Bolts, Gaskets, Packing, Jointing glue, etc. as applicable
A) Inlet Pipework- Approved Lined Ferrous Pipes and Fittings to PN 16
7.1 | 900 mm dia. Coupling (Mark A) | Nr | 1
7.2 | 900 mm dia. Flanged Spigot Pipe 1500mm long (Mark B) | Nr | 1
7.3 | 900 x 600mm dia. All Flanged Special Tee (Mark C) | Nr | 1
7.4 | 600 x 900 mm dia. All Flanged Concentric Taper (Mark D) | Nr | 1
7.5 | 600mm dia. Flanged Spigot Pipe 3000mm long. (Mark E) | Nr | 5
7.6 | 600 mm dia. Coupling (Mark F) | Nr | 9
7.7 | 600mm dia. Flanged Spigot Pipe 8000mm long. (cut to suit) (Mark G) | Nr | 3
7.8 | 600mm dia. All Flanged 90o Bend (Mark H) | Nr | 1
7.9 | 600mm dia. Plain Ended Pipe 12000 mm long (Mark I) | Nr | 4
7.1 | 600mm dia. Plain Ended Pipe 9500mm long. (cut to suit) (Mark J) | Nr | 1
7.11 | 600mm dia. Plain Ended Pipe 9000mm long. (cut to suit) (Mark K) | Nr | 1
7.12 | 600mm dia. Flange Adaptor. (Mark L) | Nr | 2
7.13 | 500mm dia. Flange Adaptor. (Mark L1) | Nr | 8
7.14 | 600x 500 mm dia. All Flanged Special Tee (Mark M) | Nr | 4
PAGE TOTAL CARRIED TO COLLECTION SHEET
7.15 | 500mm dia Spigot Flanged Pipe 1200mm long with puddle flange at 600mm from Flanged end. (Mark N) | Nr | 2
7.16 | 500mm dia. All Flanged Butterfly Valve with extension spindle, headstock and handwheel. (Mark O) | Nr | 4
7.17 | 500mm dia. All Flanged Dismantling Joint 300mm long. (Mark P) | Nr | 4
7.18 | 500mm dia All Flanged Flow Control Valve with Integrated Altitude Valve Function. (Mark Q) | Nr | 4
7.19 | 500mm dia. Flanged Spigot Pipe 2000mm long. (Mark R) | Nr | 4
7.2 | 500mm dia All Flanged Pipe 1200mm long with puddle flange at 600mm from one end. (Mark S) | Nr | 4
7.21 | 500mm dia All Flanged Pipe 2300mm long with puddle flange at 750mm from one end. (Mark T) | Nr | 4
7.22 | 500mm dia Flanged Spigot 900 Bend (Mark U) | Nr | 4
7.23 | 500mm dia. Flanged Spigot Pipe 800mm long (cut to suit). (Mark V) | Nr | 2
7.24 | 500mm dia All Flanged Pipe 1900mm long with puddle flange at 600mm from one end. (Mark W) | Nr | 2
7.25 | 500mm dia. Flanged Spigot Pipe 4700mm long. (Mark X) | Nr | 4
7.26 | 500mm dia Flanged 900 Bend (Mark Y) | Nr | 8
7.27 | 500 mm dia. Coupling (Mark Z) | Nr | 2
7.28 | 600 mm dia. Blank Flange. (Mark A1) | Nr | 2
B) Outlet Pipework - Approved Lined Ferrous Pipes and Fittings to PN 16
7.29 | 600mm dia. Special Flanged Bellmouth 400mm long with puddle flange 300mm from flanged end. (Mark 1) | Nr | 4
7.3 | 600mm dia. All Flanged 900 Bend (Mark 2) | Nr | 6
7.31 | 600mm dia. Flanged Spigot Pipe 5000mm long. (Mark 3) | Nr | 4
7.32 | 600mm dia. Coupling. (Mark 4) | Nr | 15
7.33 | 600mm dia Flanged Spigot Pipe 1400mm long with puddle flange 800mm from flanged end. (Mark 5) | Nr | 4
7.34 | 600mm dia all Flanged Butterfly Valve with Extension Spindle, headstock and Handwheel. (Mark 6) | Nr | 4
7.35 | 600mm dia. Flange Adaptor. (Mark 7) | Nr | 4
7.36 | 600mm dia Plain Ended Pipe 1400mm long with puddle flange at 800mm from one end. (Mark 8) | Nr | 4
7.37 | 600mm dia Flanged Spigot Pipe 1200mm long. (Mark 9) | Nr | 2
7.38 | 600mm dia Flanged Spigot Pipe 10600mm long (cut to suit). (Mark 10) | Nr | 2
PAGE TOTAL CARRIED TO COLLECTION SHEET
7.39 | 600mm dia. Plain Ended Pipe 12000mm long . (Mark 11) | Nr | 6
7.4 | 600mm dia. Flanged Spigot Pipe 12000mm long . (Mark 11A) | Nr | 1
7.41 | 600mm dia. Flanged Spigot Pipe 11300mm long . (Mark 11B) | Nr | 1
7.42 | 600mm dia Flanged Spigot Pipe 2000mm long (cut to suit). (Mark 12) | Nr | 2
7.43 | 700mm x 600 mm dia. All Flanged Concentric Taper (Mark 13) | Nr | 2
7.44 | 700 x 600mm dia. All Flanged Special Tee (Mark 14) | Nr | 2
7.45 | 700mm dia. Flanged Spigot Pipe 1500mm long (Mark 15) | Nr | 3
7.46 | 700mm dia. Coupling. (Mark 16) | Nr | 16
7.47 | 700mm dia. Plain Ended Pipe 12000mm long . (Mark 17) | Nr | 12
7.48 | 700mm dia Flanged Spigot Pipe 4300mm long.(cut to suit) (Mark 18) | Nr | 1
7.49 | 700mm dia. All Flanged 900 Bend (Mark 19) | Nr | 1
7.5 | 700mm dia. Flanged Spigot Pipe 5000mm long (cut to suit). (Mark 20) | Nr | 1
7.51 | 800mm x 700 mm dia. All Flanged Concentric Taper (Mark 21) | Nr | 1
7.52 | 600mm x 800mm dia. All Flanged Special Tee (Mark 22) | Nr | 1
7.53 | 700mm dia. Flanged Spigot Pipe 7300mm long (Mark 23) | Nr | 1
7.54 | 800mm dia. Flanged Spigot Pipe 1500mm long (Mark 24) | Nr | 1
7.55 | 800 mm dia. Coupling (Mark 25) | Nr | 1
7.56 | 700mm dia. Plain Ended Pipe 3200mm long . (Mark 26) | Nr | 1
C) Washout & Overflow Pipework - Approved Lined Ferrous Pipes and Fittings to PN 16
Overflow Pipework
7.57 | 700mm dia. Flanged Spigot Pipe 2700mm long with puddle flange at 100mm from spigot end (Mark 1) | Nr | 4
7.58 | 700mm dia. All Flanged Special 45o Bend (Mark 2) | Nr | 4
7.59 | 700mm dia. Flanged Spigot Pipe 2650mm long with spigot and beveled (Mark 3) | Nr | 4
Scour Pipework
7.6 | 400mm dia. Plain Ended Pipe 5500 mm long with puddle flange 100mm from one end (Mark i) | Nr | 4
7.61 | 400mm dia. Coupling (Mark ii) | Nr | 4
7.62 | 400mm dia. Flanged Spigot Pipe 1200mm long with puddle flange at 540mm from flanged end (Mark iii) | Nr | 4
7.63 | 400mm dia. All Flanged Butterfly Valve with extended spindle 2200mm long, headstock and handwheel (Mark iv) | Nr | 4
PAGE TOTAL CARRIED TO COLLECTION SHEET
7.64 | 400mm dia. Flanged Spigot 90o Bend (plain end cut to suit) (Mark v) | Nr | 4
8 | Pipes, Fittings & Valves
Transport from Site Store, Lay Joint and Test
A) Inlet Pipework- Approved Lined Ferrous Pipes and Fittings to PN 16
8.1 | 900 mm dia. Coupling (Mark A) | Nr | 1
8.2 | 900 mm dia. Flanged Spigot Pipe 1500mm long (Mark B) | Nr | 1
8.3 | 900 x 600mm dia. All Flanged Special Tee (Mark C) | Nr | 1
8.4 | 600 x 900 mm dia. All Flanged Concentric Taper (Mark D) | Nr | 1
8.5 | 600mm dia. Flanged Spigot Pipe 3000mm long. (Mark E) | Nr | 5
8.6 | 600 mm dia. Coupling (Mark F) | Nr | 9
8.7 | 600mm dia. Flanged Spigot Pipe 8000mm long. (cut to suit) (Mark G) | Nr | 3
8.8 | 600mm dia. All Flanged 90o Bend (Mark H) | Nr | 1
8.9 | 600mm dia. Plain Ended Pipe 12000 mm long (Mark I) | Nr | 4
8.1 | 600mm dia. Plain Ended Pipe 9500mm long. (cut to suit) (Mark J) | Nr | 1
8.11 | 600mm dia. Plain Ended Pipe 9000mm long. (cut to suit) (Mark K) | Nr | 1
8.12 | 600mm dia. Flange Adaptor. (Mark L) | Nr | 2
8.13 | 500mm dia. Flange Adaptor. (Mark L1) | Nr | 8
8.14 | 600x 500 mm dia. All Flanged Special Tee (Mark M) | Nr | 4
8.15 | 500mm dia Spigot Flanged Pipe 1200mm long with puddle flange at 600mm from Flanged end. (Mark N) | Nr | 2
8.16 | 500mm dia. All Flanged Butterfly Valve with extension spindle, headstock and handwheel. (Mark O) | Nr | 4
8.17 | 500mm dia. All Flanged Dismantling Joint 300mm long. (Mark P) | Nr | 4
8.18 | 500mm dia All Flanged Flow Control Valve with Integrated Altitude Valve Function. (Mark Q) | Nr | 4
8.19 | 500mm dia. Flanged Spigot Pipe 2000mm long. (Mark R) | Nr | 4
8.2 | 500mm dia All Flanged Pipe 1200mm long with puddle flange at 600mm from one end. (Mark S) | Nr | 4
8.21 | 500mm dia All Flanged Pipe 2300mm long with puddle flange at 750mm from one end. (Mark T) | Nr | 4
8.22 | 500mm dia Flanged Spigot 900 Bend (Mark U) | Nr | 4
8.23 | 500mm dia. Flanged Spigot Pipe 800mm long (cut to suit). (Mark V) | Nr | 2
PAGE TOTAL CARRIED TO COLLECTION SHEET
8.24 | 500mm dia All Flanged Pipe 1900mm long with puddle flange at 600mm from one end. (Mark W) | Nr | 2
8.25 | 500mm dia. Flanged Spigot Pipe 4700mm long. (Mark X) | Nr | 4
8.26 | 500mm dia Flanged 900 Bend (Mark Y) | Nr | 8
8.27 | 500 mm dia. Coupling (Mark Z) | Nr | 2
8.28 | 600 mm dia. Blank Flange. (Mark A1) | Nr | 2
B) Outlet Pipework - Approved Lined Ferrous Pipes and Fittings to PN 16
8.29 | 600mm dia. Special Flanged Bellmouth 400mm long with puddle flange 300mm from flanged end. (Mark 1) | Nr | 4
8.3 | 600mm dia. All Flanged 900 Bend (Mark 2) | Nr | 6
8.31 | 600mm dia. Flanged Spigot Pipe 5000mm long. (Mark 3) | Nr | 4
8.32 | 600mm dia. Coupling. (Mark 4) | Nr | 15
8.33 | 600mm dia Flanged Spigot Pipe 1400mm long with puddle flange 800mm from flanged end. (Mark 5) | Nr | 4
8.34 | 600mm dia all Flanged Butterfly Valve with Extension Spindle, headstock and Handwheel. (Mark 6) | Nr | 4
8.35 | 600mm dia. Flange Adaptor. (Mark 7) | Nr | 4
8.36 | 600mm dia Plain Ended Pipe 1400mm long with puddle flange at 800mm from one end. (Mark 8) | Nr | 4
8.37 | 600mm dia Flanged Spigot Pipe 1200mm long. (Mark 9) | Nr | 2
8.38 | 600mm dia Flanged Spigot Pipe 10600mm long (cut to suit). (Mark 10) | Nr | 2
8.39 | 600mm dia. Plain Ended Pipe 12000mm long . (Mark 11) | Nr | 6
8.4 | 600mm dia. Flanged Spigot Pipe 12000mm long . (Mark 11A) | Nr | 1
8.41 | 600mm dia. Flanged Spigot Pipe 12000mm long . (Mark 11B) | Nr | 1
8.42 | 600mm dia Flanged Spigot Pipe 2000mm long (cut to suit). (Mark 12) | Nr | 2
8.43 | 700mm x 600 mm dia. All Flanged Concentric Taper (Mark 13) | Nr | 2
8.44 | 700 x 600mm dia. All Flanged Special Tee (Mark 14) | Nr | 2
8.45 | 700mm dia. Flanged Spigot Pipe 1500mm long (Mark 15) | Nr | 3
8.46 | 700mm dia. Coupling. (Mark 16) | Nr | 16
8.47 | 700mm dia. Plain Ended Pipe 12000mm long . (Mark 17) | Nr | 12
8.48 | 700mm dia Flanged Spigot Pipe 4300mm long.(cut to suit) (Mark 18) | Nr | 1
8.49 | 700mm dia. All Flanged 900 Bend (Mark 19) | Nr | 1
8.5 | 700mm dia. Flanged Spigot Pipe 5000mm long (cut to suit). (Mark 20) | Nr | 1
PAGE TOTAL CARRIED TO COLLECTION SHEET
8.51 | 800mm x 700 mm dia. All Flanged Concentric Taper (Mark 21) | Nr | 1
8.52 | 600mm x 800mm dia. All Flanged Special Tee (Mark 22) | Nr | 1
8.53 | 700mm dia. Flanged Spigot Pipe 7400mm long (Mark 23) | Nr | 1
8.54 | 800mm dia. Flanged Spigot Pipe 1500mm long (Mark 24) | Nr | 1
8.55 | 800 mm dia. Coupling (Mark 25) | Nr | 1
8.56 | 700mm dia. Plain Ended Pipe 12000mm long . (Mark 26) | Nr | 1
C) Washout & Overflow Pipework - Approved Lined Ferrous Pipes and Fittings to PN 16
Overflow Pipework
8.57 | 700mm dia. Flanged Spigot Pipe 2700mm long with puddle flange at 100mm from spigot end (Mark 1) | Nr | 4
8.58 | 700mm dia. All Flanged Special 45o Bend (Mark 2) | Nr | 4
8.59 | 700mm dia. Flanged Spigot Pipe 2650mm long with spigot and beveled (Mark 3) | Nr | 4
Scour Pipework
8.6 | 400mm dia. Plain Ended Pipe 5500 mm long with puddle flange 100mm from one end (Mark i) | Nr | 4
8.61 | 400mm dia. Coupling (Mark ii) | Nr | 4
8.62 | 400mm dia. Flanged Spigot Pipe 1200mm long with puddle flange at 540mm from flanged end (Mark iii) | Nr | 4
8.63 | 400mm dia. All Flanged Butterfly Valve with extended spindle 2200mm long, headstock and handwheel (Mark iv) | Nr | 4
8.64 | 400mm dia. Flanged Spigot 90o Bend (plain end cut to suit) (Mark v) | Nr | 4
9 | Metalwork
All Galvanized Steelwork to be completely cleaned by acid dipping prior to galvanizing.
Supply and Install:
9.1 | Stainless steel ladders, height n.e. 6000mm installed internally in Reservoir, all as per details on Drg No. M430/SD/05-2 | Nr | 8
9.2 | Stainless steel ladders, height n.e. 6000mm installed externally in Reservoir, all as per details on Drg No. M430/SD/05-2 | Nr | 8
9.3 | Lockable mild steel chequered plate covers over inspection manholes to Reservoir size 1000mm x 1000mm. Rate to include for fabrication, installation, painting work, etc., all to Engineer's approval. | Nr | 20
9.4 | -Ditto- but lockable mild steel chequered plate covers over access manholes to Reservoir size 1000mm x 1000mm. Rate to include for fabrication, installation, painting work, etc., all to Engineer's approval. | Nr | 4
PAGE TOTAL CARRIED TO COLLECTION SHEET
10 | Miscellaneous Work
Provide and lay
10.1 | 500 gauge polythene sheeting in blinding for Base Slabs | m2 | 6600
10.2 | 150mm thick layer of pumice on roof of Reservoirs as per details in Drg. No. M30/MP/SR/DKR/04 | m2 | 6600
10.3 | Supply and Install vent pipes on roof of Reservoirs embedded into Roof Slabs | Nr | 50
10.4 | Supply and install 80mm dia. uPVC drain pipes at base of parapet wall on roof slabs at 2m c/c | Nr | 280
10.5 | Supply and install floating type calibrated staff depth measuring Gauge for water level monitoring in the Reservoirs. | Nr | 4
Water Based Epoxy Floor and Wall Coating 'MASTERTOP 1110T' or approved equivalent
10.6 | Epoxy wall and floor coating, 'MASTERTOP 1110T' or approved equivalent, on internal surfaces of Reservoir Inlet Compartments. | m² | 4700
11 | ASSOCIATED CHAMBERS AND PIPELINES
Reinforced Concrete Inlet, Outlet, Scour and Overflow Chambers to Storage Reservoir and Meter Chamber
;- 4 Nr. Reinforced concrete Inlet Valve Chambers, dimensions 4850 x 1700 x 5000mm deep. - 4 Nr. Reinforced concrete Outlet Valve Chambers, dimensions 1800 x 2000 x 4250mm deep. - 6 Nr. Reinforced concrete Scour and Overflow Chambers, dimensions 3000 x 3000 x 4300mm deep
Excavation
The rates should include for all strutting, shuttering, stabilizing the excavation faces and keeping the excavation free of water by pumping, bailing or other means.
Excavate for foundations, part backfill after construction and remainder cart away to tips or use as fill on site, all as directed by the Engineer.
11.1 | Maximum depth n.e. 1.0m | m3 | 110
11.2 | Maximum depth 1.0m to 2.0m | m3 | 110
11.3 | Maximum depth 2.0m to 3.0m | m3 | 82
11.4 | Maximum depth 3.0m to 6.0m | m3 | 34
11.5 | Extra over items 11.1 to 11.4 for excavation in rock Class 'A'. Blasting not permitted (Provisional) | m3 | 3.2
11.6 | -Ditto - but for excavation in rock Class 'B'. Blasting not permitted (Provisional). | m3 | 44
11.7 | -Ditto - but for excavation in rock Class 'C'. Blasting not permitted (Provisional). | m3 | 20
PAGE TOTAL CARRIED TO COLLECTION SHEET
Concrete Works
Supply all Materials, Mix and Place Mass Concrete Class 15/20mm Maximum Aggregate as Specified in:-
11.8 | 75mm thick blinding concrete layer under Base Slabs. | m2 | 202
Supply all Materials, Mix and Place Guaranteed Strength Reinforced Concrete Class 25/20mm Maximum Aggregate as Specified in:-
11.9 | Base slabs | m3 | 52
11.1 | Vertical Walls | m3 | 152
11.11 | Roof Slabs | m3 | 40
Supply all Materials, Mix and Place Mass Concrete Class 20/20mm Maximum Aggregate as Specified in:-
11.12 | Mass concrete stools | m3 | 4
11.13 | Mass concrete benching | m3 | 8
Reinforcement
Provide and Fix High Tensile Steel Reinforcement to SRN 127, Including Cutting, Bending, Propping with Spacers and Tying as Specified:-
11.14 | Reinforcement, all diameters | ton | 35
Formwork
Provide and Fix Shuttering including Propping, Strutting and Striking, all as Specified:-
Sawn Formwork - Class F1 finish
11.15 | Vertical formwork, width n.e 300mm | m | 280
11.16 | Vertical formwork, width exceeding 300mm | m2 | 630
Wrot Formwork - Class F3 finish
11.17 | Vertical formwork, width n.e 300mm | m | 210
11.18 | Vertical formwork, width exceeding 300mm | m2 | 560
11.19 | Horizontal formwork, width exceeding 300mm | m2 | 120
11.2 | Extra over concrete works for boxouts for pipes nominal bore n.e 900mm and making good after installation of pipework. | Nr. | 36
11.21 | - Ditto-, but for 1020mm x 1020mm Access Manhole | Nr. | 20
Metal Work
11.22 | Provide all materials and fix Stainless Steel ladder, depth n.e 3m internally in chambers, as per detail in Drg. No. M430/SD/05-2 | Nr. | 4
11.23 | Ditto but Chamber depth 3 - 5.0m internally as per detail in Drg. No. M430/SD/05-2 | Nr. | 8
PAGE TOTAL CARRIED TO COLLECTION SHEET
11.24 | Provide and fix lockable G.M.S checkered plate cover to chamber size 1020 x 1020 as per details on Drg. No. M430/SD/17-18 | Nr. | 20
Miscellaneous Works
11.25 | Provide and fix 150mm dia uPVC vent pipes to reinforced concrete wall, with plastic coated metal gauze fitted at both ends | Nr. | 112
PAGE TOTAL CARRIED TO COLLECTION SHEET
Note on C128: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Formwork width not exceeding 300mm to be measured in linear meters

## Collection Sheet Bill No. 4.1
IMPROVEMENT OF DRINKING WATER AND SANITATION SYSTEM IN MOMBASA: MWACHE CKE 1103
LOT 1: CONSTRUCTION OF THE MWACHE TWIN TRUNK MAIN (TM1), SOUTH MAINLAND TRANSMISSION PIPELINE AND DONGO KUNDU RESERVOIR
BID No. CWWDA/AFD/PQ/W4/2022-2023
BILL No. 4.1 - DONGO KUNDU RESERVOIRS (28,000 m3 CAPACITY)
Amount
(Kshs.)
Page Total, Page 1 of 13
Page Total, Page 2 of 13
Page Total, Page 3 of 13
Page Total, Page 4 of 13
Page Total, Page 5 of 13
Page Total, Page 6 of 13
Page Total, Page 7 of 13
Page Total, Page 8 of 13
Page Total, Page 9 of 13
Page Total, Page 10 of 13
Page Total, Page 11 of 13
Page Total, Page 12 of 13
Page Total, Page 13 of 13
Bill No. 4.1 Total Exclusive of VAT carried to Summary Sheet

## Bill No. 4.2
IMPROVEMENT OF DRINKING WATER AND SANITATION SYSTEM IN MOMBASA: MWACHE CKE 1103
LOT 1: CONSTRUCTION OF THE MWACHE TWIN TRUNK MAIN (TM1), SOUTH MAINLAND TRANSMISSION PIPELINE AND DONGO KUNDU RESERVOIR
BID No. CWWDA/AFD/PQ/W4/2022-2023
BILL NO 4.2 - CHLORINE STORAGE AND MIXING BUILDING
ITEM | DESCRIPTION | UNIT | QUANTITY | RATE | AMOUNT
No. |  |  |  | (Kshs) | (Kshs)
1 | SUBSTRUCTURE
Excavations and Earthworks
The rates shall include for all strutting, shuttering, stabilizing the excavation faces and keeping the excavation free of water by pumping, bailing or other means
1.1 | Excavate average 150mm deep to remove vegetable soil and cart away | m2 | 116
Bulk excavations and top soil stripping for all structures are measured under Bill No. 4.3 - Site and Ancillary Works.
Excavate below stripped level/ reduced level for foundations in common material, part backfill after construction and remainder, cart away to tips or use as fill on site, all as directed by the Engineer
Excavation Depth n.e 1.5m deep starting from stripped level/ reduced level to receive:-
1.1 | Foundations | m3 | 35
Extra over Excavation in any position for Excavation in Rock (Blasting not permitted)
1.2 | Excavation in Rock Class A (Provisional) | m3 | 1
1.3 | Ditto- But Rock Class B (Provisional) | m3 | 7
1.4 | Ditto- But Rock Class C (Provisional) | m3 | 3
Approved selected Filling
1.5 | Fill and ram selected excavated materials around foundations and buildings | m3 | 6
Approved Imported Fill as described:-
1.6 | Provide and deposit approved imported murram in maximum 150mm thick compacted layers in making up levels over 300mm thick. Rate to include for compaction to the Engineer's approval | m3 | 8
1.7 | Provide and place hand-packed 300mm thick layer of approved hardcore fill material in making up levels including achieving satisfactory compaction | m2 | 22
1.8 | Provide, lay and level out, 50mm thick fine crushed stone, sand or gravel blinding to surface of filling, including watering and rolling to achieve satisfactory compaction | m2 | 22
Disposal of Surplus Spoil:-
1.9 | Cart away surplus excavated materials to an approved dumping site | m3 | 25
Anti-Termite Treatment
1.1 | Chemical anti-termite treatment to surface of filling with approved insecticide | m2 | 26
Damp-proof Membrane
1.11 | 500 Gauge polythene sheeting, laid over hardcore | m2 | 26
PAGE TOTAL CARRIED TO BILL COLLECTION PAGE
Concrete Work:
Mass Concrete Class 15/20mm Maximum Aggregate as Specified in:-
1.12 | 50mm thick blinding concrete under foundation concrete | m2 | 26
Guaranteed Strength Reinforced Concrete Class 25/20mm Maximum Aggregate as Specified in:-
1.13 | Foundation trenches, columns and piers combined with foundation trenches | m3 | 15
1.14 | Columns and piers combined with foundation trenches | m³ | 3
1.15 | Entrance Ramp | m3 | 2
Guaranteed Strength Reinforced Concrete Class 25/20mm maximum aggregate as described in:-
1.18 | Isolated columns and piers in foundations | m3 | 2
Reinforcement
Fabric Reinforcement No. A142 Mesh Size 150 x 150mm Weighing 2.22 kgs Per m2 , Including Bends, Tying Wire and Distance Blocks:-
1.16 | Fabric reinforcement with minimum 150mm wide side and end laps, laid in bed | m2 | 22
Provide and Fix High Tensile Steel Reinforcement to BS 4449 including cutting, bending, propping with spacers and tying as specified :-
1.17 | Reinforcement, all diameters | Ton | 3
Formwork
Provide and fix shuttering including propping, strutting and striking, all as specified
Sawn Formwork - Class F1 Finish:-
1.18 | Vertical sides of columns in foundations | m2 | 23
Wrot Formwork - Class F3 Finish:-
1.19 | Edges of entrance ramp (150mm high) | m | 17
1.23 | Ditto risers of steps 75-150mm high | m | 5
1.2 | Raking open string edge of entrance steps 325mm (extreme) high including cutting top edge to profile of treads and risers | m | 2
Walling
Natural Stone Block Walling, Medium Chisel Dressed, Reinforced with 20 swg Hoop Iron at every alternate course, and Bedded, Jointed and Pointed in Cement Mortar (1:3):-
1.21 | 200 mm Walling | m2 | 32
PAGE TOTAL CARRIED TO BILL COLLECTION PAGE
2 | SUPERSTRUCTURE
CONCRETE, FORMWORK, REINFORCEMENT
Concrete
Guaranteed Strength Reinforced Concrete Class 25/20mm as Described in:
2.1 | 100mm Thick doser support slabs | m2 | 4
2.1 | Ground Floor Base Slab | m3 | 5
2.2 | First Floor Slab | m3 | 5
2.3 | Columns | m3 | 5
2.4 | Beams | m3 | 7
2.5 | External Stairs, Landings and Stair Beams | m3 | 4
2.6 | 200mm Thick Mixing Platform Slab | m3 | 1
2.7 | 200mm Thick Tank Base slab | m3 | 1
2.4 | 250mm Thick channel walls | m2 | 13
2.8 | 200mm Thick Walls | m3 | 5
2.9 | 100mm Thick Tank Wall | m3 | 1
2.9 | 150mm Thick suspended ramp laid to slope not exceeding 15 degrees from horizontal | m2 | 22
2.1 | 250mm Thick solid suspended slab | m2 | 57
2.1 | 100mm Thick Doser platform | m3 | 1
2.11 | Provide all materials and form scour and dosing pipework channel with 150mm thick RC walls internal size 300mm wide x 150mm deep in concrete floor slab including forming rebate 50mm wide x 50mm deep to top inner edges of channel wall to receive precast concrete cover slabs. | m | 7
2.12 | Labour and material in forming lip in mixing tank concrete walls and partitions, lip 75mm wide x 150mm high with 75 x 75mm chamfered bottom edge | m | 5
Formwork
Provide and fix shuttering including propping, strutting and striking, all as specified
Sawn Formwork - Class F1 Finish :-
2.13 | Horizontal and Sloping formwork | m2 | 16
2.12 | Sloping soffits of ramp not exceeding 15 degrees from horizontal | m2 | 20
2.23 | Raking open string edge of staircase 325mm (extreme) high including cutting bottom edge to profile of treads and risers | m | 2
Wrot Formwork - Class F3 Finish :-
2.14 | Vertical sides of slab and tank walls | m2 | 40
2.15 | Vertical sides of Columns and Beams | m2 | 85
2.16 | Horizontal Formwork for first floor slab soffit | m2 | 18
2.17 | Sloping Soffit of Stairs | m2 | 5
PAGE TOTAL CARRIED TO BILL COLLECTION PAGE
Reinforcement
Provide and Fix High Tensile Steel Reinforcement to BS 4449 including cutting, bending, propping with spacers and tying as specified :-
2.18 | Reinforcement, all diameters | Kg | 5150
Precast Reinforced Concrete (1:2:4) with minimum cube strength of 14 N/square millimetre at 7 days and 21 N/ square millimetre at 28 days as described in:
2.22 | Channel cover slab 800mm long x 300mm wide x 75mm thick including setting in formed rebate on top of channel wall | nr | 26
2.19 | Channel cover slab 300mm long x 300mm wide x 75mm thick including setting in formed rebate on top of channel | Nr | 20
2.22 | Channel cover slab 800mm long x 300mm wide x 75mm thick including setting in formed rebate on top of channel wall | nr | 26
2.2 | Cover slab 300mm long x 900mm wide x 100mm thick including setting in formed rebate on top of SCOUR/OVERFLOW Chamber | Nr | 3
2.22 | Channel cover slab 800mm long x 300mm wide x 75mm thick including setting in formed rebate on top of channel wall | nr | 26
2.21 | PCC Slab 600 x 600mm wide x 100mm thick around the building | m2 | 55
3 | WALLING
Natural Stone Block Walling, Medium Chisel Dressed, Reinforced with 20swg Hoop Iron at Every Alternate Course and Bedded, Jointed and Pointed in Cement Mortar(1:3)
3.1 | 200mm Thick walling | m2 | 60
Labours
3.2 | Extra over walling for ruled horizontal joints | m2 | 60
Precast Concrete Cills :-
3.3 | 200mm Thick × 275mm precast concrete cill bedded, jointed and pointed in cement mortar on top of 200mm wall. | m2 | 12
Damp -Proof Course:
Bituminous Felt Damp-Proof Course as Described:-
3.4 | 200mm Wide under walls | m | 30
Plinths
3.5 | 15mm Cement and sand (1:4) render to plinth walls, finished with wood float | m2 | 10
Precast Reinforced Concrete (1:2:4) Lintel 200mm Deep Reinforced with 4 No.10mm Diameter Mild Steel Bars and 6mm Diameter Mild Steel Link at 20mm Centres, Finished Smooth on all Exposed Surfaces, Including all Moulds and Formwork, Hoisting, Bedding and Flush Pointing in Cement and Sand Mortar (1:4):-
3.6 | Lintel 200mm wide × 1000mm long | Nr | 2
Precast Concrete Louvre Block Walling :-
3.7 | 200mm Thick louvre block walling with twin section with plastic coated coffee tray wire sandwiched between sections | m2 | 8
PAGE TOTAL CARRIED TO BILL COLLECTION PAGE
4 | ROOF COVERINGS
Single lap interlocking coloured concrete roofing tiles on and including sawn cypress (Grade 2) battens size 40 x 40mm pressure impregnated with approved preservative:-
4.1 | Roof tiles | m2 | 50
Extra over roofing tiles for:-
4.2 | Ridge capping including bedding and pointing in cement sand (1:4) mortar with colouring to match colour of tiles | m | 8
4.3 | Filled ends of ridge capping | Nr | 2
4.4 | 28 Gauge galvanized plain sheeting laid in two layers as underlay and nailed to rafters | m2 | 50
4.5 | Fair raking cutting roofing tiles | m | 21
4.6 | Fair raking cutting corrugated sheet roofing | m | 21
5 | CARPENTRY AND JOINERY
Carpentry
Roof Timbers
Double Pitch Roof Truss in Sawn Cypress Grade II Seasoned and Pressure Impregnated with Wood Preservative and timber joints with bolted and nailed connections to the Engineer's approval :-
5.1 | Equal scissor truss 6000mm clear span and 900mm high with 600mm eaves projection, in 200 x 50mm rafters and 150 x 50mm sloping ceiling joists | Nr | 3
Other Roof Members
Sawn Cypress Grade II Maximum Moisture Content 12% Seasoned and Pressure Impregnated with Wood Preservative and timber joints with bolted and nailed connections to the Engineer's approval:-
5.2 | 100 x 50mm Intermediate rafters | m | 40
5.3 | 150 x 50mm Purlins | m | 55
5.4 | 200 x 50mm Ridge board | m | 6
5.5 | 100 x 50mm Wall plate tied to wall with 20 s.w.g. hoop iron at 900mm centres | m | 17
5.6 | Scarfed joint to 200 x 50mm timber member | Nr | 5
5.7 | Scarfed joint to 150 x 50mm timber member | Nr | 4
Sundries
5.8 | Bed wall plate in cement mortar (1:3) | m | 17
PAGE TOTAL CARRIED TO BILL COLLECTION PAGE
Joinery
General Timbers
Wrot Prime Grade Cypress
5.9 | 250 x 40mm Fascia board | m | 24
6 | CEILING
12mm Thick Gypsum Board or Approved Equivalent Fixed to and including 50 x 50mm Sawn Cypress Grade 2 Battens at 600mm Centres in Both Directions Complete with Gauge Jointing and filler Material
6.1 | Ceiling laid to slope n.e 15 degrees fixed to underside of trusses | m2 | 35
6.2 | 12mm Cornice 50mm high laid to slope, plugged | m | 16
6.3 | Extra over ceiling lining for forming removable access trap door size 600 x 600mm with 100 x 38 mm sawn treated cypress trimming joists between tie beams,120 x 20mm (finished ) wrot cypress frame all round and 20mm blockboard removable panel set loose on top of framing | Nr | 1
7 | METALWORK
Steel Doors
Pressed Metal Louvre Doors
Supply and Fix the following Pressed Metal Louvre Doors with 100 x 50mm Stiles and Top Rails, 150 x 50mm Middle and Bottom Rails With Pressed Metal Infill Louvres and 100 x 50mm Pressed Metal Frames, Including Hinges, Pad Bolts and Tower Bolts, All To Manufacturer's Details, with one coat lead oxide primer complete with opening accessories including bedding and pointing around frames in cement mortar:-
7.1 | Double door size 1200 x 2400 mm high in two equal panels (D2a) | Nr | 1
7.2 | Single door size 900 x 2400 mm high (D2b) | Nr | 1
7.2 | Double door size 1600 x 2100 mm high in two equal panels | nr
7.3 | Double door size 1800 x 2500 mm high in two equal panels | nr | 1
uPVC Casement Windows
Supply and Fix the following Standard Section PVC Casement Windows, including 4mm Thick Clear Sheet Glass glazed to uPVC Casements with Putty, Complete with Opening Accessories, Including Building in Lugs to Jambs and Head and Water-Proofing and Filling Around Opening with Approved Compound; and Including Burglar-Proofing Fabricated from 12 x 12mm Mild Steel Square Bars at 150mm Centres Vertically and 150mm Horizontally and Fixed Internally to Surrounding Wall with 12mm Mild Steel Fish-Tailed Lugs at Maximum 600mm Centres; all Finished with Three Coats Oil Paint, :-
7.3 | Window size 1197 x 1197mm high with 3 equal panels, with upper part having 2nr fixed and 1nr. top being ventilator and lower half having 2nr. side hung panels opening outwards and 1nr. fixed panel to detail | Nr | 2
PAGE TOTAL CARRIED TO BILL COLLECTION PAGE
7.4 | Window size 1197 x 597mm high steel casement window in 3 equal panels with 1No. Fixed and 2No top hung panels opening outwards (W5) | Nr | 2
Balustrades and Railings
Balustrade Unit 1000mm High comprising 40mm Diameter Galvanized Pipe Top, Middle and Bottom Rails and 40mm Diameter Galvanized Pipe Balusters Spaced at Maximum 1000mm centres and bottom end bent, fanged and built into mortice in concrete, including all necessary Welding:-
7.5 | Raking Balustrade unit 9000mm long, 6000mm and 3000mm | m | 10
7.6 | Level Balustrade unit 6000mm long, 4500mm and 1500mm | m | 4
RENDERING
12.5mm Thick Cement and Sand Render as described externally on :-
7.7 | Columns | m2 | 45
7.8 | Horizontal sides and soffites of beams | m2 | 24
8 | PLASTERING
12.5mm Thick Gauged Cement Plaster as described internally on :-
8.1 | Concrete or blockwork | m2 | 150
8.2 | Reveals of openings | m2 | 5
8.3 | Sloping soffites of ramp not exceeding 15 degrees from horizontal | m2 | 19
8.3 | Sloping soffites of ramp not exceeding 15 degrees from horizontal | m² | 5
8.4 | Sloping soffites of staircase exceeding 15 degrees from horizontal | m2 | 5
8.5 | Raking open string edge of staircase 295mm (extreme) high | m | 2
8.5 | Horizontal soffites of suspended slabs | m2 | 5
Screeds
Bonded cement and sand (1:4) screed bed in one coat, well bonded to concrete base as described:-
8.6 | 38mm Thick screed laid level to receive granito floor tiling (measured separately) | m2 | 80
8.7 | 12mm (minimum) Thick Cement and sand backing (1:4) with approved plasticiser to receive granito floor laid to skirtings, treads and risers (measured separately) | m2 | 40
Bonded cement and sand (1:4) screed bed in one coat with approved hardener incorporated in the mix, well bonded to concrete base as described:-
8.8 | 38mm Thick screed laid level to receive epoxy lining (measured separately) | m2 | 50
8.9 | 150 x 20mm Thick skirting with hardener laid with a square top edge and coved junction with floor finish | m | 45
PAGE TOTAL CARRIED TO BILL COLLECTION PAGE
Floor Tiling
Acid-proof Granito Floor Tiles :-
8.1 | Floor tiles laid on screed (measured separately) with straight joints both ways | m2 | 85
8.11 | Tiles laid to risers and treads of steps on screed (measured separately) with straight joints both ways | m2 | 24
8.12 | Tiles laid as skirting 150mm high | m | 40
8.13 | Provide and fix 12mm thick Acrilin Tank Wall Tiles fixed with tile adhesive with straight joints both ways | m2 | 50
Water Based Epoxy Floor and Wall Coating as 'MASTERTOP 1110T' applied strictly in accordance with the Manufacturer's printed instruction:-
8.14 | Coating laid to floors | m2 | 39
8.15 | Coating laid to mixing tank walls and partitions | m2 | 18
8.16 | Coating laid to vertical skirting or upstand surfaces | m2 | 22
9 | GLAZING
4mm Thick Clear Sheet Glass And Glazing to Upvc Casements with putty in panes:-
9.1 | 0.10 - 0.50 Square metres | m2 | 2
9.2 | 0.50 - 1.00 Square metres | m2 | 3
10 | PAINTING AND DECORATING
Prepare, Knot, Prime, Stop and Apply Three Coats First Quality Gloss Paint to Wood Surfaces
Externally on:-
10.1 | General surfaces of fascia boards | m2 | 6
Prepare, Touch up Primer and Apply Three Coats Gloss Paint:
Externally on:-
10.2 | General surfaces of louvred metal doors (measured flat overall) | m2 | 15
10.3 | Surfaces of Balustrades and Railings | m | 12
Internally on:-
10.4 | General surfaces of louvred metal doors (measured flat overall) | m2 | 11
10.5 | Balustrades and Railings | m | 14
Prepare and apply Three Coats Exterior Quality Plastic Emulsion Paint:-
Externally on:-
10.6 | Fair-faced vertical concrete columns | m2 | 38
PAGE TOTAL CARRIED TO BILL COLLECTION PAGE
10.7 | Fair-faced horizontal sides and soffites of beams | m2 | 16
Prepare and apply Three Coats Interior Quality Plastic Emulsion Paint:-
Internally on:-
10.8 | Plastered concrete or blockwork | m2 | 118
10.9 | Ditto reveals of openings | m2 | 6
10.1 | Ditto sloping soffites of ramp n.e 15° from horizontal | m² | 5
10.11 | Ditto sloping soffites of staircase exceeding 15 ° from horizontal | m2 | 5
10.12 | Ditto raking open string edge of staircase 295mm (extreme) high | m | 2
10.13 | Plastered horizontal soffites of suspended slabs | m2 | 18
Prepare and Apply Three Washable Distemper as Described to:-
10.14 | Sloping soffites of suspended plasterboard ceilings | m2 | 40
11 | CHLORINE MIXING TANKS
Note: All technical details including type, material, specification, etc. to be submitted with Tender for all Chlorine mixing equipment and pipework. Non-submission of above requirement will result in equipment to be supplied to approval of the Engineer and cost quoted will deem to include required approved materials & equipment
11.1 | Provide and place 6mm stainless steel chemical dissolving tray as per details on Drg. No. M430/MP/SR/DK/CSMB/03 | Nr | 2
Ranges in Chlorine mixing tanks in chlorination building
Supply all equipment to site, store, install, test, commission and maintain the following ranges and equipment, including all nuts, bolts, washers, packing etc.
11.2 | Three ranges complete of 25mm uPVC pipework for water supply to chlorine mixing tanks including for making connection to domestic water supply main as per details | Item | L.S
11.3 | Three ranges complete of 50mm diameter uPVC pipes and fittings for outlet from Chlorine mixing tanks to solution feed dosers as per details | Item | L.S
11.4 | Two ranges complete of 80mm diameter uPVC pipes and fittings for overflow and for washout from Chlorine mixing tanks to SCOUR/OVERFLOW chamber as per details. Include for all anchoring and supporting of all pipework and fittings | Item | L.S
11.5 | Two ranges of pipework of 40mm diameter reinforced nylon pipe from chlorine mixing tank to 4Nr Inlet Points of Tanks; total length n.e 60m | Item | L.S
11.6 | Two ranges of 150mm dia. uPVC Pipe Sleeves from Chlorine Mixing Building to Inlet Points of 2Nr Tanks. Estimated total length 100m | Item | L.S
PAGE TOTAL CARRIED TO BILL COLLECTION PAGE
Provide and fix approved "Epofloor" lining in accordance with the manufacturer's instructions
11.7 | 5mm lining to bottom of mixing tanks | m2 | 3
11.8 | 5mm lining to sides of mixing tanks | m2 | 3
11.9 | Provide and fix gravity feed chemical dosers for hypochlorite solution dosing. Dosing Rate up to 100 ml/s, FRO Type or approved equivalent complete with outlet funnels, etc. | Nr | 2
11.10 | Provide and fix 300mm diameter exhaust extractor fan to be fixed in the chlorine mixing room and chlorine store | Nr | 3
11.11 | Provide and fix hand driven mixers for Chlorine Mixing Tanks. The plate, paddle and shaft to be of non-corrosive material. Include for fixing on tanks as shown on Drg. No. M430/MP/SR/CHR/CMSB/03 | Nr | 2
11.12 | Provide and fix 3mm thick stainless steel graduated scale as detailed | nr | 2
12 | SCOUR / OVERFLOW DRAINAGE
|  | m | 12
11.1 | Provide all materials and form Scour Chamber internal size 1200mm long x1200mm wide x 1000mm deep made out of 150mm thick reinforced concrete class 25/20 base slab and 200mm thick masonry walls including forming rebate 50mm wide x 50mm deep to top inner edges of the chamber wall to receive a precast concrete cover as shown on Drg. No. M407/CG/TW/KB/CMSB/03.
12.2 | Form rebate 50mm x 50mm for precast concrete cover slabs over the dosing pipework and scour/overflow channels. Apply 3 coats of approved epoxy paint to surfaces of rebates | m | 24
12.3 | Provide and fix precast concrete slabs 500mm x 290mm x 45mm thick, each slab coated with 3 layers of approved epoxy paint | nr | 24
12.1 | Provide all materials and form Scour Chamber internal size 1200mm long x1200mm wide x 1000mm deep made out of 150mm thick reinforced concrete class 25/20 base slab and 200mm thick masonry walls including forming rebate 50mm wide x 50mm deep to top inner edges of the chamber wall to receive a precast concrete cover as shown on Drg. No. M430/MP/SR/DK/CSMB/02. | Nr | 3
12.2 | Excavate, provide, lay and joint 150mm dia uPVC Flexible Jointed Drain Pipes, backfill after laying of pipes and cart away surplus to tips or use as fill on site, all as directed by the Engineer. Depth n.e 2m | m | 100
12.3 | Supply and install, including excavation, etc 1No Chemical Soakaway Pit / Radial Arms including Inlet Chambers and Pipework, etc all as per Supplier's instructions. | Item | L.S
13 | Electrical Works for the Chlorine Storage and Mixing Building
13.1 | Supply all materials and install appropriately rated electrical conductors and wiring, including necessary conduits system, all in line with regulatory requirements. | Item | LS
13.2 | Supply all materials and install Distribution Board and MCC Panel for Electric Mixers and Dosers, including overload protection and circuit breakers as required, connect and integrate mixers and dosers into the electrical system including control wiring for operation, corrosion resistant lighting fixtures and socket outlets suitable for hazardous environment, etc. Rate to include for testing and commissioning all electrical works for the building. | Item | LS
PAGE TOTAL CARRIED TO BILL COLLECTION PAGE
13 | CHLORINE DOSING ROOM
13.1 | Excavate for, provide all materials and construct Chlorine Dosing Room with electrical distribution, light fittings, etc., all as detailed on Drg. No. M376/K/TW/CD/01. Include for all finishes, painting, etc. | Item | L.S

## Collection Sheet Bill No. 4.2
IMPROVEMENT OF DRINKING WATER AND SANITATION SYSTEM IN MOMBASA: MWACHE CKE 1103
LOT 1: CONSTRUCTION OF THE MWACHE TWIN TRUNK MAIN (TM1), SOUTH MAINLAND TRANSMISSION PIPELINE AND DONGO KUNDU RESERVOIR
BID No. CWWDA/AFD/PQ/W4/2022-2023
BILL NO 4.2 - CHLORINE MIXING AND STORAGE BUILDING
Amount
(Kshs.)
Page Total, Page 1 of 10
Page Total, Page 2 of 10
Page Total, Page 3 of 10
Page Total, Page 4 of 10
Page Total, Page 5 of 10
Page Total, Page 6 of 10
Page Total, Page 7 of 10
Page Total, Page 8 of 10
Page Total, Page 9 of 10
Page Total, Page 10 of 10
Bill No. 4.2 Total Exclusive of VAT carried to Summary Sheet

## Bill No. 4.3
IMPROVEMENT OF DRINKING WATER AND SANITATION SYSTEMS IN MOMBASA: MWACHE CKE 1103
LOT 1: CONSTRUCTION OF THE MWACHE TWIN TRUNK MAIN (TM1), SOUTH MAINLAND TRANSMISSION PIPELINE AND DONGO KUNDU RESERVOIR
BID No. CWWDA/AFD/PQ/W4/2022-2023
BILL No. 4.3 - ADMINISTRATION BUILDING, STAFF HOUSES AND SITE AND ANCILLARY WORKS
ITEM | DESCRIPTION | UNIT | QUANTITY | RATE | AMOUNT
No. |  |  |  | (Kshs) | (Kshs.)
1 | ADMINISTRATION BUILDING/ R.E'S OFFICE
1.1 | Excavate for Foundations, supply all materials and construct Administration Building / Resident Engineer's Office as per Drg. No. M430/DK-REO/01,02,03&04 and Clause 801 of the Particular Specifications, including maintenance, water supply, sewerage, drainage, electrical supply, telephone, internet, and other facilities, all as specified, during use as the Resident Engineer's Office. The Building, furniture and equipment to revert to Employer at the end of the Contract. Include for all water supply and water borne sanitation including waste pipes, inspection chambers, Septic Tank etc. Include for KPLC Power Supply with a Meter Board. Building to be constructed using permanent building materials as per Ministry of Public Works Building By-laws or approved equivalent. Note: This is to be done as Priority Works within the first 16 Weeks after date of Mobilization. Floor area approx. 220m2 | Item | L.S
\
2 | DEMOLITION AND SITE CLEARANCE
The Employer has no available land to offer for dumping of spoil, construction debris or demolished materials. Identification of and all accruing costs related to securing suitable area of land for dumping is the responsibility of the Contractor. Dumping and spreading is to be done in accordance with existing National Legislation and Local Authority's by-laws. The Contractor to allow for this aspect of Work in his excavation, demolition and cart away to tips rates.
Excavation shall include for all strutting, shoring sides, stabilizing excavated surfaces, dewatering etc. It shall also include, trimming and compaction of excavated surfaces as required, all to the satisfaction of the Engineer.
2.1 | Clear area within the reservoir site of all grass, bushes, shrubs, hedges, grub up roots and cart away to tips identified by the Contractor in liaison with Local Authorities as directed by the Engineer | ha | 5
2.2 | Cut down trees, grub up roots and cart away to tips identified by the Contractor in liaison with Local Authorities. Girth n.e. 1.5m (Provisional) | Nr | 20
2.3 | -Ditto- but girth 1.5 - 3.0m | Nr | 10
2.4 | Stumps of diameter n.e 1.5m | Nr | 10
2.5 | Stumps of diameter 1.5m to 3.0m | Nr | 10
Top Soil Stripping
2.6 | Stripping off top 200mm deep vegetable soil within Reservoir site and stack part of material for reuse as and where directed by the Engineer, cart away surplus to tips. | ha | 5
Earthworks
Excavation including maintaining and supporting sides and keeping free from water, mud and fallen materials, part backfill and remainder cart away to tips identified by the Contractor and approved by the local authorities
PAGE TOTAL CARRIED TO SECTION COLLECTION SHEET
2.7 | Excavate area around the tank from stripped surface after removal of top soil, depth n.e. 1.0m. Stack on site selected material for reuse (surplus to be carted away under item 2.13 below) | m3 | 5000
2.8 | -Ditto - but excavation depth 1.0m to 2.0m | m3 | 5000
2.9 | -Ditto - but excavation depth 2.0m to 5.0m | m3 | 4000
2.1 | Extra Over items 2.7 to 2.9 for excavation in rock class 'A', blasting not permitted (Provisional) | m3 | 80
2.11 | -Ditto- but for excavation in rock class 'B', blasting not permitted (Provisional) | m3 | 1920
2.12 | -Ditto- but for excavation in rock class 'C', blasting not permitted (Provisional) | m3 | 800
2.13 | Cart away surplus material to tip as directed | m3 | 26000
Landscaping
2.14 | Spread top soil stacked on site (item 2.6) for reuse. Level and prepare for grassing and landscaping | m2 | 12600
2.15 | Provide and plant approved grass in areas prepared under the item above and maintain until it takes root | m2 | 12600
3 | MASONRY PERIMETER WALL FENCING AND GATES
3.1 | Provide all materials and construct Masonry Perimeter Wall around the proposed Reservoir site. Rate to include for earthworks and construction of Masonry Perimeter Wall complete with R.C. Columns on R.C. Bases at 3m c/c, R.C Ground Beam and Machine Cut Masonry Stone walling for the super-structure above Ground Beam. Masonry wall to be reinforced with Gauge 16 Hoop Iron at alternate courses. Rate to include for rendering of the walls on lower and upper courses and provision of Precast Concrete Coping with drips on both sides, all as per detail on Drawing No. M430/SD/14B and to the Engineer's approval. Masonry wall to be applied with adequate coats of approved water repelant on both faces as per manufacturer's specifications. | m | 1300
3.2 | Provide all materials, fabricate and fix double leaf vehicular access steel gate, 4m wide, including 2Nr. reinforced concrete pillars, all as per details in Drg. No. M430/SD/15 &16 | Nr | 2
3.3 | Ditto but 1m wide Gate. | Nr | 1
4 | WORKS PIPELINE
A) Supply, Transport to Site & Store in secure place including Jointing Material, Bolts, Gaskets, Packing, Jointing glue, etc. as applicable
900/800mm Dia.Ferrous Inlet Interconnection Pipeline from Mwache WTP Transmission Main to Proposed 14,000m3 Reservoir - Line''A''
PAGE TOTAL CARRIED TO SECTION COLLECTION SHEET
4.1 | 900 mm dia. Coupling. (Mark 1) | Nr | 3
4.2 | 900mm dia Plain Ended Pipe 23m long with couplings (cut to suit on site). (Mark 2) | Nr | 1
4.3 | 900mm dia. Flanged Spigot Pipe 1.5m Long. (Mark 3 ) | Nr | 2
4.4 | 900mm dia. All Flanged Pipe 1.5m long with puddle flange at 700mm from one end. (Mark 4) | Nr | 2
4.5 | 900mm dia. All Flanged Butterfly Valve with Bypass and Gear Mechanism. (Mark 5 ) | Nr | 1
4.6 | 900 mm dia. Dismantling Piece (Mark 6) | Nr | 1
4.7 | 900 x 800 mm dia. All Flanged Concentric Taper. (Mark 7 ) | Nr | 1
4.8 | 800mm dia. All Flanged 450 Bend. (Mark 8) | Nr | 4
4.9 | 800mm dia All Flanged Pipe 8m long with puddle flange at 700mm from one end. (Mark 9) | Nr | 1
4.1 | 800 mm dia. Dismantling Piece (Mark 10) | Nr | 1
4.11 | 800mm dia. All Flanged Battery Powered Electromagnetic Water Meter, minimum battery life 5yrs. (Mark 11) | Nr | 1
4.12 | 800mm dia. All Flanged Pipe 4m long with puddle flange at 700mm from one end. (Mark 12) | Nr | 1
4.13 | 800 x 900 mm dia. All Flanged Concentric Taper. (Mark 13 ) | Nr | 1
4.14 | 900 mm dia. Plain Ended Pipe 61m long with couplings (cut to suit on site). (Mark 14) | Nr | 1
4.15 | 900mm dia. Flange Adaptor. (Mark 15) | Nr | 1
4.16 | 900mm dia. Plain Ended Pipe 1.5m long. (Mark 16) | Nr | 1
900mm Dia. Ferrous Outlet Interconnection Pipeline from Proposed 14,000m3 2Nr Reservoirs to Transmission Pipeline - Line ''B''
4.17 | 800mm dia. Flanged Spigot Pipe 4m Long. (Mark A ) | Nr | 1
4.18 | 800mm dia. All Flanged 450 Bend. (Mark B) | Nr | 4
4.19 | 800mm dia. All Flanged Pipe 8m long with puddle flange at 700mm from one end. (Mark C) | Nr | 1
4.2 | 800 mm dia. Dismantling Piece (Mark D) | Nr | 1
4.21 | 800mm dia. All Flanged Battery Powered Electromagnetic Water Meter, minimum battery life 5yrs. (Mark E) | Nr | 1
4.22 | 800mm dia. All Flanged Pipe 4m long with puddle flange at 700mm from one end. (Mark F) | Nr | 1
4.23 | 800 x 900 mm dia. All Flanged Concentric Taper. (Mark G ) | Nr | 1
4.24 | 900mm dia. Flanged Spigot Pipe 1.5m Long. (Mark H) | Nr | 1
4.25 | 900 mm dia. Coupling. (Mark I) | Nr | 2
4.26 | 900mm dia Plain Ended Pipe 25m long with couplings (cut to suit). (Mark J) | Nr | 1
PAGE TOTAL CARRIED TO SECTION COLLECTION SHEET
B) Transport from Site Store, Lay Joint and Test
900/800mm Dia.Ferrous Inlet Interconnection Pipeline from Mwache WTP Transmission Main to Proposed 14,000m3 Reservoir - Line''A''
4.27 | Trench excavation, backfilling and Reinstatement after installation of fittings, depth n.e 6m. Rate to include for supply of imported fill material where necessary. Pipe dia. 900/800mm | m | 125
4.28 | Extra over excavation, backfillinng and Reinstatement item(4.27) for excavation in Rock (all classes) | m3 | 800
4.29 | 900 mm dia. Coupling. (Mark 1) | Nr | 3
4.3 | 900mm dia Plain Ended Pipe 23m long with couplings (cut to suit on site). (Mark 2) | Nr | 1
4.31 | 900mm dia. Flanged Spigot Pipe 1.5m Long. (Mark 3 ) | Nr | 2
4.32 | 900mm dia. All Flanged Pipe 1.5m long with puddle flange at 700mm from one end. (Mark 4) | Nr | 2
4.33 | 900mm dia. All Flanged Butterfly Valve with Bypass and Gear Mechanism. (Mark 5 ) | Nr | 1
4.34 | 900 mm dia. Dismantling Piece (Mark 6) | Nr | 1
4.35 | 900 x 800 mm dia. All Flanged Concentric Taper. (Mark 7 ) | Nr | 1
4.36 | 800mm dia. All Flanged 450 Bend. (Mark 8) | Nr | 4
4.37 | 800mm dia All Flanged Pipe 8m long with puddle flange at 700mm from one end. (Mark 9) | Nr | 1
4.38 | 800 mm dia. Dismantling Piece (Mark 10) | Nr | 1
4.39 | 800mm dia. All Flanged Battery Powered Electromagnetic Water Meter, minimum battery life 5yrs. (Mark 11) | Nr | 1
4.4 | 800mm dia. All Flanged Pipe 4m long with puddle flange at 700mm from one end. (Mark 12) | Nr | 1
4.41 | 800 x 900 mm dia. All Flanged Concentric Taper. (Mark 13 ) | Nr | 1
4.42 | 900 mm dia. Plain Ended Pipe 61m long with couplings (cut to suit on site). (Mark 14) | Nr | 1
4.43 | 900mm dia. Flange Adaptor. (Mark 15) | Nr | 1
4.44 | 900mm dia. Plain Ended Pipe 1.5m long. (Mark 16) | Nr | 1
900mm Dia. Ferrous Outlet Interconnection Pipeline from Proposed 14,000m3 2Nr Reservoirs to Transmission Pipeline - Line ''B''
4.45 | Trench excavation, backfilling and Reinstatement after installation of fittings, depth n.e 6m. Rate to include for supply of imported fill material where necessary. Pipe dia. 900/800 | m | 55
4.46 | Extra over excavation, backfillinng and Reinstatement item(4.45) for excavation in Rock (all classes) | m3 | 300
4.47 | 800mm dia. Flanged Spigot Pipe 4m Long. (Mark A ) | Nr | 1
PAGE TOTAL CARRIED TO SECTION COLLECTION SHEET
4.48 | 800mm dia. All Flanged 450 Bend. (Mark B) | Nr | 4
4.49 | 800mm dia. All Flanged Pipe 8m long with puddle flange at 700mm from one end. (Mark C) | Nr | 1
4.5 | 800 mm dia. Dismantling Piece (Mark D) | Nr | 1
4.51 | 800mm dia. All Flanged Battery Powered Electromagnetic Water Meter, minimum battery life 5yrs. (Mark E) | Nr | 1
4.52 | 800mm dia. All Flanged Pipe 4m long with puddle flange at 700mm from one end. (Mark F) | Nr | 1
4.53 | 800 x 900 mm dia. All Flanged Concentric Taper. (Mark G ) | Nr | 1
4.54 | 900mm dia. Flanged Spigot Pipe 1.5m Long. (Mark H) | Nr | 1
4.55 | 900 mm dia. Coupling. (Mark I) | Nr | 2
4.56 | 900mm dia Plain Ended Pipe 25m long with couplings (cut to suit). (Mark J) | Nr | 1
Scour / Overflow Drainage Pipeline
4.57 | Excavate trench for 600mm dia. Double Wall Corrugated (DWC) HDPE SN8 Socket and Spigot Jointed Pipes, including trench shoring, bedding, surrounds, backfill after laying of pipes and cart away surplus to tips or use as fill on site, all as directed by the Engineer.
4.57.1 | Depth 1.5m - 2.0m | m | 100 |  |  | 180
4.57.2 | Depth 2.0 m - 2.5 m | m | 100 |  |  | 230
4.57.3 | Depth 2.5 m - 3.0 m | m | 100 |  |  | 275
4.57.4 | Depth 3.0 m - 3.5 m | m | 100 |  |  | 325
4.57.5 | Depth 3.5 m - 5 m | m | 100 |  |  | 425
4.57.6 | Depth 5 m - 6 m | m | 100 |  |  | 550
4.57.7 | Depth 6 m - 7 m | m | 200 |  |  | 1300
4.57.8 | Depth 7 m - 8 m | m | 200 |  |  | 1500
4.58 | Provide, lay and joint 600mm dia. Double Wall Corrugated (DWC) HDPE SN8 Socket and Spigot Jointed Pipes | m | 1000
4.59 | Provide all materials, mix and place concrete Class 15/20 in bed, haunch and surround as specified, to DWC HDPE Pipes and where directed by the Engineer. | m3 | 100
4.6 | Extra over item 4.57 for excavation in rock, blasting not permitted (Provisional)
4.60.1 | Excavation in trench for rock class "A" | m3 | 700
4.60.2 | Excavation in trench for rock class "B" | m3 | 500
4.60.3 | Excavation in trench for rock class "C" | m3 | 500 |  |  | 35.53%
Chambers
4.61 | Provide all materials, excavate for and construct 1600mm x 2000mm x 2400mm deep R.C. Meter Chambers. Rate to include for Supply of formwork, excavation in all materials, supply and placing of concrete, Reinforcement steel, curing etc. Supply, fixing and constructing of access ladders, ventilation, drainage, etc. All to detail and as specified in Drg. No. M430/SD/06 | Nr | 2
4.62 | Ditto but for Line Valve Chamber dimensions 350 x 2400mm deep | Nr | 1
4.63 | Excavate for, provide all materials, special shuttering etc. and construct 1200 mm dia. internal dimensions Reinforced Concrete chambers. Include for building in pipes, forming benching to falls, Composite FRP manhole cover, Access Ladders,Ventilation, etc. all as detailed. Depth to invert n.e. 1.0m | Nr | 4
4.64 | Ditto but for depths 1-2m | Nr | 4
4.65 | Ditto but for depths 2-3m | Nr | 4
4.66 | Ditto but for depths 3-4m | Nr | 4
4.67 | Ditto but for depths exceeding 4m | Nr | 4
PAGE TOTAL CARRIED TO SECTION COLLECTION SHEET
5 | ROADS AND FOOTPATHS
Roads
5.1 | Excavate below stripped surface to formation levels for roads, buildings, etc., and stack part of material for use as and where directed by the Engineer, cart away surplus to tips. (Provisional) | m3 | 2000
5.2 | Extra Over excavation items for excavation in rock Class 'A' for roads and footpaths (Provisional) | m3 | 16
5.3 | -Ditto- but rock Class 'B' | m3 | 240
5.4 | -Ditto- but rock Class 'C' | m3 | 40
5.5 | Fill using approved excavated material and compact in 150 mm layers as specified under roads and verges | m3 | 2000
5.6 | Provide and apply approved weed killer to the murram base as specified for Roads and Footpaths | m2 | 2100
Concrete Block Paved Roads
Sub-Base and Base Courses: Provide, Lay and Compact:
5.7 | Hand packed hardcore compacted to CBR not less than 30 up to formation level (where road is in fill) | m² | 1700
5.8 | Base 200mm thick crusher run or quarry chips (hand packed), including for watering and stone dust blinding as directed. | m2 | 1700
5.9 | Provide and apply approved weed killer / herbicide to road surface in accordance with manufacturer's instructions | m2 | 1700
Concrete Block Paving (as Manufactured by Cabro Works Ltd or Other Approved Supplier)
5.1 | Heavy duty loading blocks size 210mm x 105mm x 80mm (Minimum strength 47N/m2) laid on and including 50mm screeded sand bed and compacted by surface vibration | m2 | 1700
Kerbs and Channels
5.11 | Provide, lay and joint 255 mm x 125 mm precast concrete kerbs on and including 250 mm x 100 mm Class 15/20 concrete foundation and haunch 125 mm thick including all excavation, shuttering, jointing and bedding as specified. | m | 900
5.12 | E.O. Item for kerbs laid to radius n.e. 3.0 m | m | 100
5.13 | Provide, lay and joint 125mm x 100mm precast concrete channels on and including 225mm x 125mm Class 15/20 concrete bed and haunch 100mm thick including all excavation, shuttering, jointing and bedding as specified. | m | 400
5.14 | E.O item for channels laid to radius n.e. 3.0m | m | 50
Footpaths
5.15 | Excavate below stripped level average 300mm deep (provisional) | m2 | 100
5.16 | 150mm thick compacted murram sub-base for footpaths, well compacted. | m2 | 100
PAGE TOTAL CARRIED TO SECTION COLLECTION SHEET
5.17 | 50mm thick compacted sand layer | m2 | 100
5.18 | Precast Concrete Paving Slabs, 600 x 600 x 50mm thick, jointed with lime and sand (1:3) | m2 | 100
Pavements around Proposed Reservoir
5.19 | Excavate below stripped level average 300mm deep (provisional) | m2 | 120
5.2 | 150mm thick compacted murram sub-base for footpaths, well compacted. | m2 | 120
5.21 | 50mm thick compacted sand layer | m2 | 120
5.22 | Precast Concrete Paving Slabs, 600 x 600 x 50mm thick, jointed with lime and sand (1:3) | m2 | 120
6 | SURFACE WATER DRAINAGE
Precast Concrete Drains
6.1 | Excavate trench for precast concrete invert block drain Type 'A' as shown on the standard drawings , including trimming of sides and cart excavated material to tips. Depth to invert n.e. 1.0m | m | 350
6.2 | -Ditto- but depth to invert 1.0m - 2.0m | m | 100
6.3 | Provide, lay and joint precast concrete invert block drain Type 'A' on 100mm murram bed, including 75mm murram filling both sides for height of block. Rate to include for all cutting, waste, etc. | m | 300
6.4 | Extra over item D above for provide, lay and joint two courses (one each side) of precast concrete side slabs to Type 'A' drain on 75mm thick compacted murram bed | m | 100
6.5 | -Ditto- but plus 4 Courses (two on each side) | m | 50
Earth Drains
6.6 | Excavate trapezoidal earth drains type 1 as shown on the standard drawings to the lines and levels directed by the Engineer. Allow for trimming of sides to correct slopes and cart excavated material to tips. Depth to invert n.e. 1.0m | m | 750
6.7 | -Ditto- but depth to invert n.e. 2.0m | m | 200
6.8 | Provide and spread 100mm of approved top soil on the base of sides of the earth drain, rake and level to the required profiles as directed by the Engineer (Provisional) | m2 | 3100
6.9 | Supply and plant approved grass on base and sides of the earth drain and maintenance until it takes root to the satisfaction of the Engineer (Provisional) | m2 | 3100
Culvert Pipes
6.1 | Excavate trench depth n.e. 2.5 m, supply, lay and joint for 600mm diameter precast concrete ogee pipes including concrete surround, backfill after laying of pipes, compact and cart away surplus material to tips. | m | 15
PAGE TOTAL CARRIED TO SECTION COLLECTION SHEET
6.11 | Excavate trench depth n.e. 2.5 m, supply, lay and joint for 300mm diameter precast concrete ogee pipes including concrete surround, backfill after laying of pipes, compact and cart away surplus material to tips. | m | 15
Headwalls
6.12 | Excavate for, provide all materials and construct 225 mm thick masonry headwalls including concrete Class 20/20 footings as detailed in Drawing No. M430/SD/21 | Nr | 6
7 | SLOPE PROTECTION
7.1 | Provide all material and carry out laying of 2mx1mx1m rock filled Gabion, Maccaferri or approved equivalent. Gabion boxes to be laid in stretches with 0.5m overlap, mesh wire to be galvanized and minimum diameter 5mm. Include for tying of adjacent gabion with approved wire and 16mm dia. anchor rods to suit site conditions (Provisional). | Nr | 200
7.2 | Provide, fill and compact in 200 mm layers imported approved excavated material as backing to gabions as directed by the Engineer. Compaction tests to be done and rates to include for this. (Provisional) | m3 | 400
7.3 | Provide and spread 50 mm thick mass concrete layer on exposed surfaces of the gabions . (Provisional) | m3 | 25
7.4 | Provide and carry out hydraulic mulch grass seeding to slopes as specified in the Drawings or as directed by the Engineer | m² | 1000
7.5 | Supply and plant approved grass on slopes and maintenance until it takes root to the satisfaction of the Engineer | m² | 1000
8 | ELECTRICAL WORKS (PROVISIONAL)
On-Site Power Connection
8.1 | Allow PC sum of Kshs. 5,000,000 for on-site power connection from the KPLC National Grid. | Item | P.C | 5000000 | 5000000
Street Lighting
8.2 | Supply and install 5.0m Columns with single arm for street lighting including suitable foundation | Nr | 25
8.3 | 3200 Lumens Integral Solar Street Light complete with battery to Engineer's approval. | Nr | 25
8.4 | 120W LED Area flood light | Nr | 25
8.5 | Supply Install and connect 6.0mm2 X 3 core PVC/SWA Cable in cable trenches and ducts | m | 1200
8.6 | Supply and install cable glands | Nr | 50
8.7 | Trenching, laying, tiling and backfilling for underground cables - Avg. depth 600mm | m | 450
8.8 | Supply and install lucy connector complete with 5Amp H.R.C fused cut-outs in the column window | Nr | 25
PAGE TOTAL CARRIED TO SECTION COLLECTION SHEET
8.9 | 2.5mm2 twin plus earth cable between Lucy Cut-out in each of the poles and the lighting fixture | m | 200
8.1 | Supply and install 16mm dia. x1500mm long earth electrode for alternate columns complete with 6mm2 copper earth wire | Nr | 14
8.11 | Supply and install cable markers | Nr | 40
8.12 | Supply and install lables on columns/ Danger warninng notices as may be necessary | Item | 1
8.13 | Engrave security lighting lanterns as required by the Engineer | Nr | 25
9 | GUARD HOUSE
9.1 | Provide all materials, Excavate for Foundations and construct 1Nr. Guard House Building complete with electrical distribution, light fittings, plumbing works, water supply and drainage works, etc., all as detailed on Drg. No. M430/MP/SR/DK/GR/01 Include for all finishes, paintings, etc. | Item | L.S
10 | STAFF HOUSE
10.1 | Excavate for foundations, supply all materials and construct 2Nr. Double Unit Semi-detached Staff Houses (Type C houses). Each house 80 m² has 2 Nr. Units as shown on Drgs. Nos. M430/MP/SR/DKR/01-04 Include for building and provision of plumbing works, inspection chambers, sewer pipes, water supply, storage tank and electrical installation, furniture and other facilities all to the approval of the Engineer. | Item | L.S
11 | ON SITE WATER SUPPLY
11.1 | Allow a Provisional Sum of Kshs 2,500,000 for provision of water supply to the Site. Items covered include | Item | P.S |  | 2500000
a) Replenishing of water in the plastic tank using a bowser during construction stage
b) Provision of an offtake from Mwache - Dongo Kundu Pipeline after construction completion
c) Provision of Materials and erecting of 5m high RC Tower for Water Tank with ladder, walkway and guard rails
d) 10,000 Litre Capacity Plastic Water Tank
e) Associated Pipework and Fittings for Reticulation within the Site
f) Testing and Sterilization of Tank and Pipework
All as directed by the Engineer.
11.2 | Allow a Provisional Sum of Kshs 500,000 for installation and commissioning of Rain Water Harvesting system from Administration Block Building, Guard House and Staff Houses as directed by the Engineer. | Item | P.S | 500000 | 500000
11.3 | Add …….% for profit, administration, attendance upon, overheads, etc. for Items 11.1 and 11.2 above. | % | 3000000
PAGE TOTAL CARRIED TO SECTION COLLECTION SHEET
12 | FOUL SEWERAGE
Pipeline Excavation
12.1 | Excavate trench for 160mm diameter DWC HDPE SN8 Drainage pipes, backfill after laying of pipes and cart away surplus to tips as directed by the Engineer. Depth not exceeding 2.0m (all depths to inverts) | m | 300
Pipeline Construction
12.2 | Provide, lay, joint and test 160mm diameter DWC pipes Class SN8 with flexible (rubber ring) joints on granular or concrete bed and surround. | m | 300
Chambers
12.3 | Excavate for, provide all materials, special shuttering etc. and construct 600mm x 450mm internal dimensions in-situ concrete inspection chambers on sewers diameter n.e 160mm. All as per the standard drawings. Include for building in pipes, forming benching to falls, Composite FRP Manhole covers, etc. Depth to invert n.e. 2.0m | Nr | 11
12.4 | Excavate for, provide all materials, special shuttering etc. and construct 1200 mm x 1200 mm internal dimensions concrete chambers . All as per the standard drawings. Include for building in pipes, forming benching to falls, Composite FRP manhole cover, etc. Depth to invert n.e. 2.0m | Nr | 5
Septic Tank
12.5 | Supply and install, including excavation, etc, 1 No. Plastic Septic Tank, minimum capacity 2.5m3, including Inlet and Outlet Chambers and Pipework, R.C. Cover Slab with access manhole, Soak Pit / Radial Arms, ventilation pipework, etc. all as per suppliers instructions ("Septank" as manufactured by Kentainers Ltd. or approved equivalent) and as directed by the Engineer. | Item | L.S
13 | CHEMICAL SOAK PIT
13.1 | Excavate for, provide all materials, construct, test and commission chemical soak away pit, including radial arms, cover slab, access manhole, ect. as detailed in Drawing No.M430/SD/22 | Nr | 1
14 | SIGNBOARD
14.1 | Provide all materials and construct publicity signboard as detailed on the standard drawings for the Site. Include for painting, decorating and anchoring of the signboard to the ground using 300mm x 300mm x 600mm deep mass concrete footing, all as detailed | Nr | 1
NOTE: FINAL WORDING ON THE SIGN BOARD TO BE DECIDED IN CONSULTATION WITH THE EMPLOYER
PAGE TOTAL CARRIED TO SECTION COLLECTION SHEET
15 | INTERCONNECTION TO EXISTING SOUTH MAINLAND DISTRIBUTION SYSTEM
15.1 | Allow a Provisional Sum of Kshs. 150,000,000/- (Kenya Shillings One Hundred and Fifty Million) for Topographycal Survey, Detailed Design and Construction of 2.5km DN 800 Ferrous Pipeline from the proposed Dongo Kundu Reservoir Outlet, interconnecting to the existing Mombasa South Mainland Distribution Network at the Southern Bypass Road, including Aerial Crossing at the Southern Bypass Road Crossing to the approval of the Road Authorities. | Item | PS | 150000000 | 150000000
16 | MISCELLANEOUS
16.1 | Allow a Provisional Sum of Kshs. 5,000,000 to be used for any other Works or items that may be required on site as directed by the Engineer. | Item | PS | 5000000 | 5000000
PAGE TOTAL CARRIED TO SECTION COLLECTION SHEET

## COLLECTION SHEET BILL 4.3
IMPROVEMENT OF DRINKING WATER AND SANITATION SYSTEM IN MOMBASA: MWACHE CKE 1113
LOT 1: CONSTRUCTION OF THE MWACHE TWIN TRUNK MAIN (TM1), SOUTH MAINLAND TRANSMISSION PIPELINE AND DONGO KUNDU RESERVOIR
BID No. CWWDA/AFD/PQ/W4/2022-2023
BILL No. 4.3 - ADMINISTRATION BUILDING, STAFF HOUSES AND SITE AND ANCILLARY WORKS
Amount
(Kshs.)
Page Total, Page 1 of 11
Page Total, Page 2 of 11
Page Total, Page 3 of 11
Page Total, Page 4 of 11
Page Total, Page 5 of 11
Page Total, Page 6 of 11
Page Total, Page 7 of 11
Page Total, Page 8 of 11
Page Total, Page 9 of 11
Page Total, Page 10 of 11
Page Total, Page 11 of 11
Bill No. 4.3 Total Exclusive of VAT carried to Summary Sheet |  | 0

## Bill No. 5.1
IMPROVEMENT OF DRINKING WATER AND SANITATION SYSTEM IN MOMBASA: MWACHE CKE 1103
LOT 1: CONSTRUCTION OF THE MWACHE TWIN TRUNK MAIN (TM1), SOUTH MAINLAND TRANSMISSION PIPELINE AND DONGO KUNDU RESERVOIR
BID No. CWWDA/AFD/PQ/W4/2022-2023
BILL No. 5.1 - INSTRUMENTATION
ITEM | DESCRIPTION | UNIT | QUANTITY | RATE | AMOUNT
No. |  |  |  | (Kshs) | (Kshs)
NOTES:
This Bill of Quantities (Bill No. 5.1) covers the supply and installation of the instrumentation for the transmission lines and reservoirs.
1 | Water transmission pipeline
1.1 | Supply, installation, wiring, connections and calibration of a transmitter for a DN 800 electromagnetic flow meter. | Nr. | 1
1.2 | Supply, installation, wiring, connections and calibration of a transmitter for a DN 900 electromagnetic flow meter. | Nr. | 1
2 | Kaya Bombo Site
2.1 | Supply, installation, wiring, connections and calibration of a transmitter for a DN 250 electromagnetic flow meter. | Nr. | 1
2.2 | Supply, installation, wiring and connections for an ultrasonic water level sensor. | Nr. | 2
2.3 | Supply, installation, wiring, connections and calibration of a transmitter for an ultrasonic water level sensor. | Nr. | 2
2.4 | Supply, installation, wiring and connections for a chlorine analyser. | Nr. | 2
2.5 | Supply, installation, wiring, connections and calibration of a transmitter for a chlorine analyser. | Nr. | 2
3 | Dongo Kundu Site
3.1 | Supply, installation, wiring, connections and calibration of a transmitter for a DN 800 electromagnetic flow meter. | Nr. | 3
3.2 | Supply, installation, wiring and connections for an ultrasonic water level sensor. | Nr. | 4
3.3 | Supply, installation, wiring, connections and calibration of a transmitter for an ultrasonic water level sensor. | Nr. | 4
3.4 | Supply, installation, wiring and connections for a chlorine analyser. | Nr. | 2
3.5 | Supply, installation, wiring, connections and calibration of a transmitter for a chlorine analyser. | Nr. | 2
PAGE TOTAL CARRIED TO COLLECTION SHEET

## Collection Sheet Bill No. 5.1
IMPROVEMENT OF DRINKING WATER AND SANITATION SYSTEM IN MOMBASA: MWACHE CKE 1103
LOT 1: CONSTRUCTION OF THE MWACHE TWIN TRUNK MAIN (TM1), SOUTH MAINLAND TRANSMISSION PIPELINE AND DONGO KUNDU RESERVOIR
BID No. CWWDA/AFD/PQ/W4/2022-2023
BILL No. 5.1 - INSTRUMENTATION
Amount
(Kshs.)
Page Total, Page 1 of 1
Bill No. 5.1 Total Exclusive of VAT carried to Summary Sheet

## Grand Summary
GRAND SUMMARY
LOT 1: CONSTRUCTION OF THE MWACHE TWIN TRUNK MAIN (SECTION 1), SOUTH MAINLAND TRANSMISSION PIPELINE AND DONGO KUNDU RESERVOIR
BID No. CWWDA/AfD/MWCE/W-TM/01/2022
BILL No. | DESCRIPTION |  | AMOUNT
(Kshs)
1 | Preliminary and General Items
2.1 | Twin Trunk Main Section 1 (Line TM)
Supply of Pipes, Fittings, Valves and Ancillaries
2.2 | Twin Trunk Main (Line TM)
Pipeline Construction
3.1 | South Mainland Water Transmission Pipeline (Line SM)
Supply of Pipes, Fittings, Valves and Ancillaries
3.2 | South Mainland Water Transmission Pipeline (Line SM)
Pipeline Construction
4.1 | Dongo Kundu Reservoir (28,000m3 Capacity)
4.2 | Chlorine Storage and Mixing Building
4.3 | Administration Building, Staff Houses and Site & Ancillary Works
5.1 | Instrumentation
| Bills Total Exclusive of VAT | (A)
| Add 7.5% of (A) for General and Physical Contingencies | (B)
| Bill Total Inclusive of Contingencies [A + B] | (C)
| Value Added Tax (VAT) - 16% of (C) | (D)
| GRAND TOTAL CARRIED TO LETTER OF BID | (C+D)
Bills Total Exclusive of VAT | (A)
Add 10% of (A) for Contingencies | (B)
Bill Total Inclusive of Contingencies | (C)
Value Added Tax (VAT) - 16% of (C) | (D)
GRAND TOTAL CARRIED TO LETTER OF BID [(C) + (D)]